## Table 6.1
1 | Structure and location of Power Generating Facility
| 1.1 | Single line diagram
| 1.2 | Structure
Type of Power Generating Facility (e.g. wind power, solar power, biomass, gasification)
Basic data (e.g. on Wind Power Park Module: tower height, rotor diameter, converter operation etc.)
| 1.3 | Location data (municipality, area, Connection Point, coordinates)
2 | Technical details of Power Generating Facility transformer(s):
| 2.1 | Number of transformers influencing the Reactive Power capacity of the Power Generating Facility
| 2.2 | Design values ​​of Power Generating Facility transformers
Power [MVA]
Current [A]
Transformer ratio [primary/secondary]
Control range and control step of off-load tap changer or on-load tap changer [%,%]
Number of steps and selected step of off-load tap changer or on-load tap changer [quantity, status data]
3 | Technical details of Power Generating Facility:
| 3.1 | Number of generator units
| 3.2 | Supplier(s) of generator units
| 3.3 | Type(s) of generator units
| 3.4 | Design values ​​of generator units
Power (apparent) [MVA]
Rated Capacity [MW]
Current [A]
Voltage [V]
Frequency [Hz]
Electric parameters of Synchronous Power Generating Modules (resistances, reactances, etc.), see Table 6.5
| 3.5 | Dependence of Production Power on the operating conditions (e.g. wind velocity, temperature)
| 3.6 | Potentially used compensation devices and/or devices used for the correction of power factor
Type(s)
Number(s)
Design values ​​(power, current, voltage, frequency)
If used for the filtering of harmonics, data on the structure and tuning frequency
4 | Power Generating Facility operational characteristics:
The following items may be replaced for example by the manufacturer's device documents, testing documentation or other testing documentation
| 4.1 | Description of Reactive Power generation capacity, and PQ diagrams of generators
| 4.2 | Description of the ability of the Power Generating Facility to operate at undervoltage and overvoltage
| 4.3 | Description of the ability of the Power Generating Facility to operate at underfrequency and overfrequency
| 4.4 | Description of the ability of the Power Generating Facility to operate during voltage disturbances
| 4.5 | Description of the supply of fault current of the Power Generating Facility during voltage disturbance
| 4.6 | Description of potential control features of the Power Generating Facility
| 4.7 | Description of the impact of the Power Generating Facility on the power quality
5 | Protection details of the Power Generating Facility:
| 5.1 | Relay protection diagram of the Power Generating Facility
| 5.2 | Final relay protection settings of the Power Generating Facility
| 5.3 | Description of the operating principle of island protection
6 | Commissioning documents:
| 6.1 | Commissioning records
| 6.2 | Final set values ​​and Mode of Reactive Power control

## Tables 6.2­6.4
1 | Data to be delivered in stage 1 of the compliance monitoring process of the Specifications
1.1 | Basic data, structure and location of Power Generating Facility
1.1.1 | Single line diagram
The main components of the Power Generating Facility and the electricity network that connects the components
Electric parameters of the components and conductors presented in the single line diagram
1.1.2 | Structure
Type of Power Generating Facility or Turbine Generators (e.g. wind power, hydropower, condensing power)
Basic data (e.g. on Wind Power Park Module: tower height, rotor diameter, full-converter etc.)
1.1.3 | Location data (municipality, area, Connection Point, coordinates)
1.2 | Reactive Power capacity of the Power Generating Facility
1.2.1 | Reactive Power capacity calculation (section 12.2.3 or 17.2.3)
1.2.2 | PQ diagrams of generators
PQ diagrams of generators and data on their voltage-frequency dependence
1.2.3 | Other components influencing Reactive Power (section 17.2.2 )
Components that generate (e.g. STATCOM) and consume Reactive Power, and their operation as a function of the variables (e.g. voltage, Active Power) influencing the components
1.3 | Technical details to be delivered of the Power Generating Facility and generators
The data shall be delivered about the Power Generating Facility as a whole and separately about each individual generator
1.3.1 | General data
Number, supplier and type details of Turbine Generator units
1.3.2 | Documentation and data sheets
Apparent power [MVA], Rated Capacity [MW], maximum output [MW], Minimum Output [MW], current [A], voltage [V], frequency [Hz]
General description of the principles of Frequency Control and Active Power control; description of the implementation and functionalities of the control system, or alternatively a detailed description of the Power Generating Facility controllers (chapter 11 or 16)
General description of the principles of voltage control and Reactive Power control; description of the implementation and functionalities of the control system, or alternatively a detailed description of the Power Generating Facility controllers (chapter 13 or 18)
Start-up times of the Power Generating Facility to Minimum Output and Rated Capacity
1.3.3 | Voltage and frequency operating ranges (section 10.2.1)
Description of operation at undervoltage and overvoltage
Description of operation at underfrequency and overfrequency
1.3.4 | Data on the operation of the Power Generating Facility in momentary voltage disturbance (section 10.2, 10.3 or 10.4)
Calculation of the operation of the Power Generating Facility during voltage disturbance, and potential reports of factory testing
Description of the current injection of the Power Park Module during voltage disturbance
Description of the power restoration of the Power Generating Facility after voltage disturbance
1.3.5 | Description of the operation of the Power Generating Facility in house load operation (section 11.2.6)
Magnitude of House Load of the Power Generating Facility, operating time in house load operation, potential delays in terms of transition to house load operation and synchronisation with the grid, and restrictions in terms of transition to house load operation
1.3.6 | Changes in Generation Power
Changes in Generation Power in conjunction with frequency and voltage fluctuations
Dependence of Output Power on the operating conditions (e.g. temperature, wind velocity)
Operating conditions leading to the shutdown of Generation Power (e.g. limit value of maximum wind velocity)
Rate of change of Active Power, functionality and constraints of limiters of rate of change
1.4 | Data to be submitted on transformers and other Power Generating Facility components
The data shall be provided on each transformer influencing Reactive Power capacity and on every other Power Generating Facility component separately. The other components are devices which have an influence on the operation of the Power Generating Facility in terms of the Specifications (e.g. compensating devices, harmonic filters, reserve power feed units etc.).
1.4.1 | General data
Number, supplier and type details
1.4.2 | Documentation and data sheets of transformers
Power [MVA], current [A], transformation ratio [primary, secondary], short-circuit impedance [%], short-circuit resistance [%], vector group and earthing details, control range and step of on- or off-load tap-changer [%, %], number of steps of on- or off-load tap-changer and selected step [quantity, step]
1.4.3 | Documentation and data sheets of other components
As applicable, the same data as on generators (section 1.3) and transformers (section 1.4) as well as all data that is relevant in terms of the Specifications (e.g. structure, tuning frequency)
1.5 | Modelling data
General data required for the modelling of the Power Generating Facility, or simulation models in accordance with the Specifications (section 15 or 20)
1.6 | Specific studies
Required specific studies related to the Specifications (chapter 4)
1.7 | Real-time measurement data
Description of the method in which the real-time measurement data is delivered to Fingrid (chapter 8)
1.8 | Preliminary schedule of Power Generating Facility project
Preliminary schedule of the project and the planned timing of the Compliance Testing relating to the Specifications. Potential options for the expansion of the project and known future expansion plans shall also be reported.
2 | Data to be delivered in stage 2 of the compliance monitoring process of the Specifications
2.1 | Changes and further specifications
Further specifications to the data required in stage 1 of the compliance monitoring process of the Specifications
2.2 | Protection settings of the Power Generating Facility and impact on the power quality
2.2.1 | Protection settings (section 9.1.2)
Preliminary data on the relay protection diagram of the generators and on facility-level relay protection diagram as well as on the primary settings of the protection described. Related data shall be submitted on protection which leads to the disconnection of the generator/facility from the grid and on protection whose functioning leads to a restriction or automatic change of the Active Power, Reactive Power or voltage of the generator/facility.
2.2.2 | Description of the impact of the Power Generating Facility/generator on the power quality (section 9.1.3)
Description of the change in the power quality caused by the connection of the Power Generating Facility to the grid, and potential reports of factory testing
2.2.3 | Description of the operating principle of potential island protection
Operating principles and restrictions when shifting to island operation and when re-synchronising after island operation
2.3 | Frequency Control and Active Power control of Power Generating Facility
2.3.1 | Documentation and description (chapter 11 or 16)
Specified documentation, at the transfer function level as applicable (functional, not detailed), concerning the implementation and operating principles of Frequency Control and Active Power control of the Power Generating Facility/generator.
2.3.2 | Settings of controllers
Preliminary parameters and operating delays set in controllers
2.4 | Voltage control and Reactive Power control of Power Generating Facility
2.4.1 | Documentation and description (chapter 13 or 18)
Specified documentation, as applicable at the transfer function level (functional, not detailed), concerning the implementation and operating principles of voltage control and Reactive Power control of the Power Generating Facility/generator.
2.4.2 | Settings of controllers
Preliminary parameters and operating delays set in controllers
2.5 | Data required for dynamic modelling
Project-specific data or simulation models required for the dynamic modelling in accordance with the Specifications (chapter 15 or 20)
2.6 | Data related to Compliance Testing
2.6.1 | Commissioning plan (section 14.3.1 or 19.3.1)
The detailed commissioning plan, including the Compliance Testing plan, preliminary commissioning instructions provided by the Power Generating Facility supplier and a description of the practical arrangements of the tests for the compliance monitoring of the Specifications shall be submitted to Fingrid for comments.
2.6.2 | Preliminary Compliance Testing schedule (section 14.3.1 or 19.3.1)
Preliminary Compliance Testing schedule; subsequent changes to the preliminary schedule shall be reported to the Relevant Network Operator and to Fingrid.
2.6.3 | Measurement arrangements (section 14.3.1 or 19.3.1)
Plan of the execution of measurements for the tests related to the Specifications. Data on both fixed measuring equipment and on measuring equipment only used during the Compliance Testing.
3 | Data to be delivered in stage 4 of the compliance monitoring process of the Specifications
3.1 | Changes and further specifications
Further specifications to the data required in stages 1 and 2 of the compliance monitoring process of the Specifications
3.2 | Results of Compliance Testing
A commissioning report of the tests related to the Specifications and primary results of the Compliance Testing in Numerical format in accordance with the Specifications (section 14.3.3 or 19.3.3)
3.3 | Verified modelling data
Validated data required for the modelling of dynamic operation, or simulation models (chapter 15 or 20)
3.4 | Final controller settings
Final reference values and settings of the controllers of Active Power and frequency as well as Active Power and voltage of the Power Generating Facility/generators
3.5 | Final protection settings
Final reference values and settings of the protection of the Power Generating Facility/generators and of the Power Generating Facility connection

## Table 6.5
1 | Rated values
1.1 | Rated voltage Ur | [kV]
1.2 | Voltage range | [p.u.]
1.3 | Apparent power Sr | [MVA]
1.4 | Rated capacity Pmax | [MW]
1.5 | Rated current Ir | [A]
1.6 | Rated power factor cos ϕr
1.7 | Rated speed of rotation n | [1/min]
1.8 | Nominal excitation voltage Ue | [V]
1.9 | Nominal excitation current If | [A]
2 | Impedances
2.1 | Stator resistance R | [p.u.]
2.2 | Direct-axis synchronous reactance Xd | [p.u.]
2.3 | Direct-axis synchronous reactance Xd (saturated) | [p.u.]
2.4 | Quadrature-axis synchronous reactance Xq | [p.u.]
2.5 | Direct-axis transient reactance Xd' | [p.u.]
2.6 | Direct-axis transient reactance Xd' (saturated) | [p.u.]
2.7 | Quadrature-axis transient reactance Xq' | [p.u.]
2.8 | Direct-axis subtransient reactance Xd" | [p.u.]
2.9 | Quadrature-axis subtransient reactance Xq" | [p.u.]
2.10 | Stator stray reactance Xl | [p.u.]
2.11 | Zero phase-sequence reactance X0 | [p.u.]
2.12 | Negative phase-sequence reactance X2 | [p.u.]
3 | Time constants
3.1 | DC short-circuit time constant Ta | [s]
3.2 | Direct-axis transient open circuit time constant Tdo' | [s]
3.3 | Quadrature-axis transient open circuit time constant Tqo' | [s]
3.4 | Direct-axis subtransient open circuit time constant Tdo" | [s]
3.5 | Quadrature-axis subtransient open circuit time constant Tqo" | [s]
3.6 | Direct-axis transient short-circuit time constant Td' | [s]
3.7 | Quadrature-axis transient short-circuit time constant Tq' | [s]
3.8 | Direct-axis subtransient short-circuit time constant Td" | [s]
3.9 | Quadrature-axis subtransient short-circuit time constant Tq" | [s]
4 | Mechanical parameters
4.1 | Stored energy constant (generator + turbine) H | [s]
4.2 | Moment of inertia of generator Jg | [kgm²]
4.3 | Moment of inertia of each turbine Jt1, Jt2, Jt3,.... | [kgm²]
4.4 | Moment of inertia of exciter (if available) Jexc | [kgm²]
4.5 | Spring constants between the above-mentioned turbine generator parts Kt1_t2 , Kt2_t3 ,..., Ktx_g , Kg_exc | [Nm/Rad]