Fingrid Oyj

Application for approval of a reserve unit for Automatic Frequency Restoration Reserve (aFRR)

[Name of the Reserve Provider] [Name of the Reserve Unit] Date [DD-MM-YYYY]

# Introduction

Reserve provider shall fill in this form for each reserve unit that they wish to offer to the automatic frequency restoration reserve market. Sections 1–3.1 of the form should be filled in before the prequalification test and sent to Fingrid for approval.  The rest of the form is completed after the prequalification test and submitted with the prequalification test results. The information requested in the form is mandatory, and it must be supplemented, if necessary, at Fingrid's request. The application form is based on Appendix 2 of the Automatic Frequency Restoration Reserve Market Agreement: The technical requirements and the prequalification process of Automatic Frequency Restoration Reserve (aFRR) [1] and on Requirements on Reliability of Reserve Provision [3].

The application and the required attachments are submitted to the My Fingrid portal.

# Summary

Type of the reserve unit: ☐ Single reserve resource ☐ Aggregated reserve unit ☐ Contractual Balancing Service Provider ☐ Independent Aggregator Name of the reserve unit: Prequalification date: Reason for the application: ☐ New reserve unit ☐ Periodic renewal of prequalification ☐ Increasing the capacity of a previously prequalified unit ☐ Significant change in the reserve unit If the reason is a significant change, please describe the change below: Indicate if type approval is being applied for: ☐ Yes ☐ No If the reason for the application is to increase the capacity of a previously qualified unit, which of the following best describes the situation: ☐ Only the new resource is tested. The resource fulfills the requirements independently. ☐ Increasing the capacity of a previously qualified resource. The resource is tested with higher capacity. ☐ Reserve unit is tested again as a whole Type of reserve unit: ☐Production ☐ Consumption ☐ Energy storage ☐ Other, what?

Fill in applied reserve capacities for each product in Table 1.

Table 1. Applied reserve capacities up and down

|  | Maximum capacity | Minimum capacity |  |
| --- | --- | --- | --- |
| CaFRRup |  |  | MW |
| CaFRRdown |  |  | MW |

# Overview

## Name of the balancing service provider

Fill in Table 2 the name of the company that will be acting as a balancing service provider (BSP) for the reserve unit in question. Balancing service provider is the party that will be signing reserve market agreement with Fingrid. If the prequalification test is carried out by another company, please fill in the name of the company performing the prequalification test.

Table 2. Name of the balancing service provider

| Name of the balancing service provider |  |
| --- | --- |
| Name of the company performing the prequalification test |  |

## Information on the reserve unit

Fill in Table 4 the information about the reserve unit. If an aggregated reserve unit includes many individual resources (logging the resources in a table is not reasonable), log the sum rated power of the aggregated portfolio partaking in the prequalification test and describes resources in more detail in Chapter 3.4.

Table 3. Information on the reserve unit

|  | Reserve Resource 1 | Reserve Resource 2 | [….] |
| --- | --- | --- | --- |
| Name |  |  |  |
| Technology |  |  |  |
| Rated power [MW] |  |  |  |

# Description of the reserve unit

## Technical data

Please provide any technical information that may be relevant for the evaluation of your application.

Below are examples of such data. For technologies other than the ones listed below, similar information should be provided.

Production resources:

- Minimum and maximum power [MW]

- Other factors that may limit the reserve activation (e.g. permitted flow rate of a hydro unit and how it is considered in the maintained reserve capacity).

Consumption resources:

- Type of consumption and its properties

- Minimum and maximum power [MW]

- Possible factors that may limit the reserve activation (e.g. thermal capacity of an electric boiler)

Energy Storages:

- Rated power [MW]

- Rated energy capacity of the energy storage [MWh]

- Available energy capacity of the energy storage [MWh]

- Upper and lower limits of energy storage state of change [MWh or %]

## Control system and signal processing

Describe the control system of the reserve unit:

> Provide a top-level description of the controller's operation (e.g., block diagram, controller parameters)

> If the reserve unit can deliver multiple reserve products or other frequency controls (FCR, FFR, FRR, LFSM), describe how simultaneous delivery is executed:

- Include a general description of the activation of different reserves, the dependencies between them, changes in the operating mode of the controller, etc.

- Describe the method that ensures that there is enough capacity for all the maintained reserve products.

- Notify if limited frequency sensitive modes (O-LFSM, U-LFSM) are defined for the unit and describe how they are implemented in the control system.

## Aggregation

If the application concerns aggregated reserve resources, describe how the aggregation system works:

>Describe the aggregated reserve resources. If type approval is applied for, include a description of the resource to be type approved.

>If type approval of a single resource is verified by prequalifying an aggregated portfolio, describe why this is done.

> Describe the operation of the aggregation system, e.g. What logic is used to activate individual resources?

> If the aggregated reserve resources come from different balances, provide a description of how the balance responsibility information for the reserve resources is kept up to date. In the case of independent aggregation, the balance responsibility data for the reserve resource must be maintained on an open supplier (RE, electricity vendor) and metering grid area (MGA) basis.

## Limitations of energy storages

> Describe the strategy for maintaining the energy storage state of charge.

> Describe how activation, deactivation, energy management etc. are implemented when delivering multiple reserve products simultaneously.

- Describe how to ensure a compliant minimum energy reservation for aFRR (1 h per direction).

## Calculation of maintained reserve capacity

> Describe how the maintained aFRR capacity (that is included in the real-time data exchange) is calculated. Indicate how often the value will be updated. See examples in source [1] chapter 6.

## Calculation of activation power

> Describe how the aFRR activation power (that is included in the real-time data exchange) is calculated. For example, include calculation formulas and possible signal processing. Indicate how often the value will be updated.

## Calculation of reference power (baseline)

If the power of the reserve unit varies according to the conditions, describe the variation and its causes.

> Describe how variations in the power of the reserve unit are considered when determining the available reserve capacity for trading. For example, what forecasts are used, how accurate are the forecasts, what margin is used, etc.

> Describe how the baseline power of the reserve unit is calculated during operation.

- Example: a reserve unit has a controlled setpoint that determines the baseline power.

- Example: the baseline power is dependent on the wind speed. Describe how it is calculated (e.g. measurement data and models used, accuracy of data/calculation, refresh interval...). Examples of calculations and more detailed requirements for validating baseline power for weather-dependent production and variable consumption can be found in the source [2]. Attach the one-month data on calculated and measured instantaneous power required in source [2], if not already provided.

## Recording of historical data

Describe the method used for continuous recording of measured values. If different measurement arrangements are used during the prequalification test, they are described in section 5.2.

> Indicate where the historical data is stored and how long it will be stored.

> Specify the time zone to use for timestamping.

# Requirements for the reliability of reserve provision

The questions presented in this chapter are based on the Requirements for the reliability of reserve provision [3]. The requirements document is available on Fingrid's website.

Fill in the Tables in subsections 4.1 and 4.2 in yes/no format. If the answer is "No" or the implementation deviates from the requirement, describe the deviation and any compensating controls in the Attention / additional information column. The questions in Tables 4 and 5 do not cover all Requirements for the reliability of reserve provision, therefore please check the compliance of your implementation with a separate requirements document [3].

If the reserve provider related to this application has a company-wide ISO27001 certification and the information systems of any trading and control systems are located in the EU's internal market, table 4 can be left unfilled. In this case, the reserve provider must submit the certificate to the MyFingrid Reserve Market service.

## Cybersecurity

Table 4. Cybersecurity requirements.

| Requirement | Yes | No | Attention / Additional Information |
| --- | --- | --- | --- |
| Requirement 1: Does the provider comply with good practices in the fields of physical and cybersecurity? Examples of good practices in the industry include training personnel, continuous development of operations, assigning responsibility for safety, comprehensive risk management, and getting the company's management to approve the operating models used. | ☐ | ☐ |  |
| Requirement 1: Are the trading and control systems located in the Internal Market area of the European Union? | ☐ | ☐ |  |
| Requirement 2: Is multi-factor authentication (MFA) enabled before accessing the components of the control or trading system? | ☐ | ☐ |  |
| Requirement 2: Are IP restrictions used in interface connections whenever it is technically feasible? | ☐ | ☐ |  |
| Requirement 3: Are logs collected from access management, jump hosts, and application events, and are logs kept for at least 6 months? | ☐ | ☐ |  |
| Requirement 3: Are logs and alerts for critical and essential services monitored 24/7/365 by a SOC (Security Operations Center)? | ☐ | ☐ |  |
| Requirement 4: Are the access rights limited by work tasks and is their necessity reviewed regularly? | ☐ | ☐ |  |
| Requirement 5: Are remote access and management connections limited to essential functions and protected by strong authentication (MFA)? | ☐ | ☐ |  |
| Requirement 6: Are system components regularly updated and vulnerabilities regularly monitored? | ☐ | ☐ |  |
| Requirement 7: Are API and management connections encrypted according to requirements (e.g. TLS 1.2/1.3, AES256 or stronger)? | ☐ | ☐ |  |
| Requirement 8: Are critical or controllable devices blocked from direct unnecessary internet connections? | ☐ | ☐ |  |
| Requirement 9: Do control and remote connections as well as jump hosts have up-to-date endpoint security protection? | ☐ | ☐ |  |
| Requirement 10: Is the Incident Response process documented, approved by provider’s management and up to date? | ☐ | ☐ |  |

## Physical security

The physical security requirements apply to providing units with an approved product-specific reserve capacity of at least 10 MW. For smaller units, the requirements are recommendations. The same limitations and recommendations apply also to centralised control and trading systems.

Table 5. Requirements for physical safety.

| Requirement | Yes | No | Attention / Additional Information |
| --- | --- | --- | --- |
| Requirement 1: Does the property have an intruder alarm system connected to a 24/7 security control room? | ☐ | ☐ |  |
| Requirement 2: Is the protection of rooms with windows located on the ground level implemented with intrusion detectors? | ☐ | ☐ |  |
| Requirement 3: Does the site have a functioning camera surveillance system, the recordings of which are stored for at least 30 days and from which there is a real-time remote connection to the control room? | ☐ | ☐ |  |
| Requirement 4: Are the functionality of burglar alarm and camera surveillance systems inspected regularly and are deficiencies corrected without delay? | ☐ | ☐ |  |

## Detection of disturbances and response capability

> Describe how connection failures or any other anomalies, such as a power failure or equipment failure, are detected and reported to maintenance/operator.

> Describe the areas covered by monitoring. Describe at least how to monitor the status and control of reserve units, the connections between the control system and the reserve unit and the measuring devices, and alarms related to physical safety and cybersecurity.

> Inform the response and repair times for disturbances in the reserve provision.

> Describe how the fault tolerance testing is organized and how often it is done (e.g. in connection with the annual clock or updates).

## Requirements for centralised control systems

> If activation is controlled from a centralized system, describe the architecture and IT security related practices. The following topics can be used as a baseline for the description. In the scope of the description, please note chapter 3.1 of the Requirements for the Reliability of Reserve Provision.

- High level description of the system architecture

- Redundancy (e.g. duplicating central functions and local fallback solutions)

- Segmentation (e.g. system’s internal segmentation based on bidding areas, when the related BSP is operating within multiple bidding areas)

- IT support of centralized control system

## Requirements for centralised trading system

> If the reserve unit receives information about the capacity to be maintained from a centralized trading system, describe the related practices. The following topics can be used as a baseline for the description. In the scope of the description, please note chapter 3.2 of the Requirements for the Reliability of Reserve Provision.

- Time and verification of the signal delivery

- IT support of the trading system

- Reserve unit operation during a connection break

# Prequalification test and results

## Overview of the prequalification test

Indicate the time and place of the prequalification test:

Describe the general operating conditions during the tests:

> Include a brief description of how the operating conditions can be expected to have affected the test result.

Describe the activation and deactivation of aFRR:

> Are there any delays? If yes, describe their reasons.

## Test Method

Describe how the reserve unit was tested:

> Describe the test method and activation sequence. Was the activation signal generated programmatically or was the signal received from Fingrid?

>Add a graph of the test results

## List of attachments

Write a summary of all attachments (e.g. test data)

> Before submitting the data, ensure that the measurement data does require manual processing before reviewing the results (remove empty rows from the beginning of the file, etc.).

## Formatting of the measurement data and naming the result file

Submit the measurement results as shown in Table 6 using the standard CSV format, where the values are separated by a comma (,), the decimal separator is a period (.) and the record separator is a carriage return. The timestamp format is ISO 8601.

Table 6. Formatting of the measurement data

| NAME | dateTime | instantaneous_power | reference_power | activated_afrr | activation_signal |
| --- | --- | --- | --- | --- | --- |
| FORMAT | YYYMMDDThhmmss.nnn | double | double | double | double |

The file is named in the format [resource name]_aFRR_[test direction]_[yyyymmdd].csv

In the case of a contractual balancing service provider or an independent aggregator, a column delivered_energy is added to Table 2 for the delivered balancing energy to check the energy calculation. The contractual balancing service provider reports the results per balance responsibility, and the independent aggregator reports the results per open supplier (RE, electricity retailer) and per metering grid area (MGA).

# References

| [1] | The technical requirements and the prequalification process of Automatic Frequency Restoration Reserve (aFRR) |
| --- | --- |
| [2] | Guideline for variable production and consumption in automatic reserves, available on Fingrid’s website |
| [3] | Requirements for the Reliability of Reserve Provision, available on Fingrid’s website |