## Introduction
NOTE: Read Grid Code chapters 6.4.3.2 in VJV2024 and SJV2024
Main Purpose of this excel is review the initial technical data for the project and its key design principles. In this excel the technical topics are highlighted which atleast must be considered in early design phase of the power plant or energy storage system or hybrid power plant, even before placing the Purchase Orders. Topics listed in this excel are based on the experience from the past projects. Also New requirements (2024), which are greatly affecting to the design are introduced.
Step by step instructions for the Connectee for Stage 0 meeting
1. Request project specific grid data from Fingrid (SCR, VCSCR, ESCR -values)
2. Request Specific Study requirements from Fingrid (Grid Code Chapter 5)
3. Go through sheet "Stage 0 Questionaire" with relevant engineers and relevant parties in your Project
4. Fill the data and the feedback from OEM(s) you have for the chapters
5. Arrange meeting with Fingrid and relevant network operator (if there is DNO)
6. Agree the next steps

## Stage 0 Questionaire
| Stage 0 Pre-design phase |  |  |  | Referred chapter |  | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
1 | General data |  |  |  | VJV2024 | SJV2024
1.1 | Name of the project (used in connection enquiry)
1.2 | Type of the power plant (Wind, Solar, BESS etc.)
1.3 | Connection point
1.4 | Grid Owner of the connection point
1.5 | Estimated date to start the production? (Target date for ION )
1.5 | Rated power of the power plant [MW] (active power at HV-side of main transformer(s))
1.6 | Installed capacity [MW] (e.g how many turbines and what rating)
1.7 | Has fault current levels and voltage control tuning data (VCSCR) been requested already from vikavirrat@fingrid.fi?
1.8 | Has evaluation of Specific Study requirements (chapter 5) already been requested from Fingrid?
1.9 | Has the Grid Code Consulant already been chosen? Who will run the simulation studies?
2 | Is this the first time that the supplier of turbines or inverters delivers the project in Finland?
2.1 | Has the Relevant Operator (RO) been chosen?
2.2 | Is it scheduled that the planning data is delivered to Fingrid six months before start of the production? (Before ION)
| 2.2.1 | Aware of new PSS/E v36 version requirement and latest modelling instructions?
2 | Specific study requirements
2.1 | Operation in IBR dominated Grid
| 2.1.1 | Low ESCR and VCSCR values - can the plant operate in stable manner? (Converter OEM should verify this)
| 2.1.2 | Specific pre-studies to be done to show this before choosing the supplier? (Stage-0 screening)
2.2 | Is the plant located in SSO area?
| 2.2.1 | SSO damping - DFIG OEM has SSO damping function? How to benchmark it, ie how to evaluate performance?
| 2.2.2 | SSO protection - to be implemented at unit level (at turbines) or at substation level?
2.3 | Is POD required by Fingrid? - (this is rarely needed)
2.4 | Specific protection or control arrangements? Temporary connections?
2.5 | Geomagnetically induced currents (GIC)? - especially on 400 kV connectees
2.6 | Power Quality ? - If required - monitoring devices and intsrument transformers
3 | Top-level Control Philosophy
3.1 | Reference point for Voltage Control (POM)
3.2 | Reference point(s) for Active power Control (POM(s))
3.3 | Reactive power limits at the point of connection (reactiver power window)? How this is taken into account in control design?
| 3.3.1 | LDC or Vref set-point optimization?
| 3.3.2 | If Line Droop Compensation (LDC) is used, is this the first time OEM is about to implement this in Finland?
| 3.3.3 | Compensation of the connectiong line needed during no production (night for solar power, not windy for wind power)?
3.4 | How many Power Park Controllers (PPC) will there be at site?
3.5 | Is the PPC supplier same as the converter supplier?
3.6 | Is there redundancy or fall-backs regarding to Power Park Controllers (PPC) if e.g Master controller fails?
3.7 | What happens for the Power Park Controller (PPC) in event of measurement failure? |  |  |  | Chapter 18 | Chapter 13
| 3.7.1 | This will be tested in test 11) in VJV2024 and test 10) in SJV2024 |  | include these in the specifications! | Chapter 19 | Chapter 15
4 | Balance of Plant
4.1 | Is there a need for point-on-wave switching i.e single pole operated breakers according to YLE2021?
4.2 | Main transformers
| 4.2.1 | What is the Un at HV-side? (note 110 kV system operation voltage is 118 kV and 400 kV system is 410 kV) |  |  | Chapter 10
| 4.2.2 | Start point arrangements; Reactor needed ? Resistors needed for GIC by Fingrid? (especially 400 kV connectees)
| 4.2.3 | Is there On-load tap changer (OLTC)? If no, has this been considered in reactive power capacity calculations?
| 4.2.4 | Connection to overhead line?
If yes, is the transformer zk high enough for Fingrid's protection selectivity requirement? (YLE2021)
4.3 | Disturbance and Swing recorders chosen and location clear? |  |  |  | Chapter 9
| 4.3.1 | Continuously measuring device? |  |  | Chapter 9
| 4.3.2 | Can they meet the measurement accuracy and data storage as required? |  |  | Chapter 9
| 4.3.3 | How to ensure that Fingrid will receive records within 8 hours after requests? |  |  | Chapter 9
4.4 | Protection design shall consider that the plant will not trip during LVRT/HVRT, voltage and frequency dips or other grid events
| 4.4.1 | Note new high voltage ride through requirement
| 4.4.2 | If overhead line connection to Fingrid - has "Local disconnection relay" included?
4.5 | Voltage and active power control implemented at site CT's and VT's (no measurements from FG's substation is allowed!)
5 | General Performance requiremets
5.1 | Reactive power requirement - is the point of requirement clear (HV side of main transformer) ? |  |  |  | Chapter 17
|  | Is there need for capacitor banks? If yes - does it have detuning reactors? Does it have specific breaker? Overvoltage protections? |  |  | Chapter 17
5.4 | Is the supplier aware of the active power priorization requirement, if the LVRT mode is not activated? |  |  |  | Chapter 10 and 18
5.6 | Is this the first time the inverter supplier and power park controller supplier deliver a project together?
| 5.6.1 | If yes, are you aware of communication risks regarding to delays and grid compliance? How to mitage the risk (FAT's?)?
| 5.6.2 | If no, how to ensure that voltage control response requirement is met regarding to communication/protocol delays?
6 | Performance requirements for Wind and Solar (ONLY VALID FOR WIND AND SOLAR PROJECTS)
6.2 | Is the supplier aware of new requirement of voltage control tuning? (fast rise time min 5 % / 30 ms)? |  |  |  | Chapter 18
|  | Has the supplier confimed e.g by simulation models and FAT tests that they have the technology for the requirement? |  |  | Chapter 18
6.3 | Is the supplier aware of the new fault current infeed requirements? |  |  |  | Chapter 18
6.4 | Has the new HVRT requirement noted in the design? Is the turbine/converter OEM aware of this? |  |  |  | Chapter 10
7 | Performance requirements for BESS (ONLY VALID FOR ENERGY STORAGE PROJECTS)
7.1 | Has the supplier been informed about the Grid Forming (GFM) requirements? |  |  |  |  | Chapter 10
7.2 | Is this the frist time the inverter supplier delivers Grid Tied Grid Forming inverter?
| 7.2.1 | If yes, how to mitigate risk of not fullfilling Fingrid's requirements regarding to GFM?
7.3 | Is this the first time the inverter supplier and power park controller supplier deliver a project together?
| 7.3.1 | If yes, are you aware of communication risks regarding to delays and grid compliance? How to mitigate the risk?
| 7.3.2 | If no, can they meet the requirements of Fingrid regarding to communication/protocol delays?
7.4 | Has the new HVRT requirement noted in the design? Is the converter OEM aware of this? |  |  |  |  | Chapter 10
7.5 | How to ensure safe disconnection from the grid if there will be Islanding? (GFM BESS can not rely on local EVY)
8 | Remote Controllability and Power Park controller
8.1 | Is the power park controller supplier aware of new signals required to be exchanged / controlled by the operator? |  |  |  | Chapter 10 | Chapter 10
8.2 | Is the Relevant Operator (RO) aware of new signals required to be changed/ controlled? |  |  |  | Chapter 10 | Chapter 10
8.3 | Is control priorization between RO,OEM, Aggregator etc. clear how to implement it in the PPC ? |  |  |  | Chapter 10 | Chapter 10
| 8.3.1 | This is tested in test 12) VJV2024 and test 11) SJV2024 |  |  | Chapter 19 | Chapter 15
8.4 | Autonomous connection after losing external network connections has this been designed? |  |  |  | Chapter 10 | Chapter 10
| 8.4.1 | This is tested in test 13) VJV2024 and test 12) SJV2024 |  |  | Chapter 19 | Chapter 15
9 | Telecommunications and information security
9.1 | Telecommunications and information security - has this been considered? |  |  |  | Chapter 10 | Chapter 10
9.2 | Have you considered any redundancy for the connections?
9.3 | Has NCER requirements considered in the project already?