Fingrid PSCAD simulation model review report (KJV2018)

Demand Facility Name: 		Data Center X

Connection Process Stage:	Stage 1 (ION) /Stage 2 (FON)

Model package:		Model_delivery_v_12345.zip

| Facility Short Circuit Data | R (Ohm) | X (Ohm) |
| --- | --- | --- |
| SCR Normal |  |  |
| SCR Minimum |  |  |

| Power data | P (MW) |
| --- | --- |
| Maximum active power Pmax (1.0 pu) |  |

# Documentation

|  | Model documentation complies (Yes/No) | Name of document and page number from where the needed item is documented |
| --- | --- | --- |
| Version history |  |  |
| General Information |  |  |
| Overview |  |  |
| Parameters |  |  |
| Usage instructions |  |  |
| Functionalities |  |  |
| Supplementary documentation |  |  |

# Modelling

|  | Model complies (Yes/No) | Comments |
| --- | --- | --- |
| Aggregation |  |  |
| Aggregation (general aggregation and OHL/cable modelling) |  |  |
| Equipment |  |  |
| Transformer parameters and equipment (saturation, OLTC, grounding configuration, etc) |  |  |
| Auxiliary equipment (compensation equipment, MOVs, filters etc.) |  |  |
| House load |  |  |
| Control signals and parameters |  |  |
| “Static” control settings (not required to be adjustable in runtime, adjustment of any given setting must not require changes in more than one location), should include at least: - Active power (and reactive power, if applicable) control settings (ramp rates, etc.) - Protection activation levels and time settings - Activation levels, deactivation levels and other relevant settings of different operation modes |  |  |
| Runtime control signals and parameters (must be adjustable in runtime) - Load active power (and reactive power, if applicable). Signal available for each individual demand unit |  |  |
| Monitoring signals |  |  |
| Relevant signals for unit and facility level controls - Protection signals - Activation and deactivation of operation modes (e.g. ride-through modes, current limiting/blocking modes) - PLL output signal (for systems using phase-locked loop synchronization) |  |  |
| Model delivery format |  |  |
| model does not include any - global substitutions - radio links - multiple layers - PNI setups |  |  |
| The full demand facility model must be stored inside single main PSCAD module with just POC connection point and acceptable signal interfaces coming out |  |  |
| Main electrical circuit must be accessible down to LV terminals of individual demand units. Black-boxing only allowed for control and protection systems of individual active demand units such as UPS. |  |  |
| Real hardware code must be embedded in the model following the IEEE/CIGRE DLL standard |  |  |
| Model dependencies are placed in single sub-folder. No unnecessary or obsolete files shall be included. |  |  |
| Model does not include any .exe files |  |  |
| Model does not include any unnecessary or duplicate definitions or obsolete objects/component |  |  |
| Stage 2 update |  |  |
| (Only for Stage 2 models) Model corresponds to the final parametrisation of the facility after the KJV tests |  |  |

# Compatibility and usage

The following tests verify that the model includes all capabilities which are required for the model to work in all the use-cases where Fingrid will be using the model (and which are not tested already in the grid code functionalities part later)

| Test # | Test | Active power | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| C1 | Version compatibility | N/A | Model runs with PSCAD version, Fortran compiler and Visual Studio version specified by Fingrid | N/A | No errors with the specified version or compiler |  |  |
| C2 | Scaling and multiple instances | N/A | Model supports multiple (>50) instances in same simulation, with separate parametrization (inc. scaling) of different instances. | N/A | No errors with multiple instances, scaling or separate parametrization of different instances |  |  |
| C3 | Multiple run and snapshot features | N/A | Model supports multiple run and snapshot features | N/A | No errors with multiple run or snapshot features |  |  |
| C4 | Initialization | 1.0 | Flat run until model is in steady state | SCR Normal | Model initialized to steady state in less than 3 seconds |  |  |
| C5 | Compatibility with TSO system model | N/A | Model behaves as expected and runs without errors in TSO system model | N/A | No issues when integrating the model to the system level model |  |  |

# Grid code functionalities

The following tests verify that the model works according to the corresponding grid code requirements.

| Test # | Test | Active power | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| G1.1 | Change of load profile | According to profile | Demand facility operational point is changed accordingly to different operation modes of the real demand facility. | SCR Normal | Load profile can be changed |  |  |
| G1.2 | Adjusting load active power | Variable P | Adjusting the load from 0 to 100 % and vice versa | SCR normal | Active power can be changed. Stable operation. |  |  |
| G2.1 | Operating limits - Voltage - Full power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G2.2 | Operating limits - Voltage - Partial power | 0.2 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G2.3 | Operating limits - Frequency - Full power – UFLS enabled | 1.0 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz, Rate of change 2 Hz/s. UFSL enabled. | SCR Normal | Expected response |  |  |
| G2.4 | Operating limits - Frequency - Full power – UFLS disabled | 1.0 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz, Rate of change 2 Hz/s. UFLS disabled | SCR Normal | Expected response |  |  |
| G3.1 | Step change in frequency | 1.0 pu | Frequency 50 Hz -> 49 Hz -> 50 Hz -> 51 Hz -> 50 Hz. Rate of change 2 Hz/s. | SCR Normal | Expected response |  |  |
| G4.1 | Compensation equipment logic disconnect | Variable P | Ramp or step change depending on the implementation logic of compensation | SCR Normal | Compensation devices shall be connected at the beginning and shall be disconnected during the active power ram |  |  |
| G4.2 | Compensation equipment logic connect | Variable P | Ramp or step change depending on the implementation logic of compensation | SCR Normal | Compensation devices shall be disconnected at the beginning and shall be connected during the active power ramp |  |  |
| G5.1 | Current limiter activation | 1.0 pu | Ramp voltage down to current limitation activation threshold and then back up to 100 % | SCR normal | Expected results |  |  |
| G5.2 | Current blocking activation | 1.0 pu | Ramp voltage down to current block activation threshold without causing a trip and then back up to 100 % | SCR normal | Expected results |  |  |
| G6.1.1 | Fault ride through – and post-fault active power recovery | 1.0 pu | 3-ph SC with 200 ms fault time | SCR normal after fault SCR minimum | Expected results |  |  |
| G6.1.2 | Fault ride through – and post-fault active power recovery | 1.0 pu | 3-ph SC with 200 ms fault time and with residual voltage U = 0.25 pu | SCR Normal | Expected results |  |  |
| G6.1.3 | Fault ride through – and post-fault active power recovery | 1.0 pu | 2-ph SC with 200 ms fault time | SCR Normal, after fault SCR minimum | Expected results |  |  |
| G6.1.4 | Fault ride through – and post-fault active power recovery | 1.0 pu | 2-ph SC to ground with 200 ms fault time | SCR Normal, after fault SCR minimum | Expected results |  |  |
| G6.1.5 | Fault ride through – and post-fault active power recovery | 1.0 pu | 1-ph ground fault with 200 ms fault time | SCR Normal, after fault SCR minimum | Expected results |  |  |
| G6.1.6 | Fault ride through – and post-fault active power recovery | 1.0 pu | 1-ph ground fault with 200 ms fault time tested on all phases with residual voltage U ≈ 0.6 pu | SCR Normal, after fault SCR minimum | Expected results |  |  |
| G6.2 | Overvoltage withstand capability | 1.0 pu and 0.2 pu | PCC Voltage 1.0 pu -> 1.2 (5 s.) pu-> 1.1 pu | Infinite bus - Forced voltage to PCC | Expected results |  |  |
| G6.3 | Multiple FRT 1 | 1.0 pu | Fault and reconnection cycle. 3-ph SC. 100 ms fault time @ T+0 s, T+0.5 s, T+1.0 s, T+30.0 s, T+35.0 s | SCR Normal | Expected results |  |  |
| G6.4 | Multiple FRT 2 | 1.0 pu | Fault and reconnection cycle. 10 consecutive 100 ms bolted 3-ph SC during same simulation. 5 second intervals. | SCR Normal | Expected results |  |  |
| G6.5 | Switchover to high voltage backup supply (if applicable) | 1.0 pu | Switchover to external high voltage backup connection (for example from 400 kV to 110 kV backup supply) | SCR Normal | Expected results |  |  |
| G7.1 | Network vector shift | 1.0 pu and 0.2 pu | Vector shift +30° and -30° without fault | SCR normal and minimum | No tripping, no undamped oscillation |  |  |
| G7.2 | Interarea oscillations | 1.0 pu | Inject 0.2-1.0 Hz voltage oscillations in dq reference frame to the POC | SCR Normal | No amplifying oscillations |  |  |
| G7.3 | Forced oscillations (if applicable) | Variable P | Agreed load profile of the demand facility used | SCR Normal | Forced oscillations from the load profile seen as expected at the PCC |  |  |
| G7.4 | Impedance scan | 1.0 pu and 0.2 pu | Impedance scan to be done from 1.0 Hz to 45 Hz | Infinite bus - Forced voltage to PCC | Expected results |  |  |
| G8.1 | High voltage protection | 1.0 pu | Voltage raised until demand facility trips | Infinite bus - Forced voltage to PCC | Demand facility trips and user will be notified about the protective function. |  |  |
| G8.2 | Low voltage protection | 1.0 pu | Voltage lowered until demand facility trips | Infinite bus - Forced voltage to PCC | Demand facility trips and user will be notified about the protective function. |  |  |
| G8.3 | High frequency protection | 1.0 pu | Frequency raised until demand facility trips | SCR Normal | Demand facility trips and user will be notified about the protective function. |  |  |
| G8.4 | Low frequency protection | 1.0 pu | Frequency lowered until demand facility trips | SCR Normal | Demand facility trips and user will be notified about the protective function. |  |  |