Fingrid PSCAD simulation model review report (SJV2024)

Power Plant Name: 		Power Plant X

Connection Process Stage:	Stage 1 (ION) / Stage 2 (FON)

Model package:		Model_delivery_v_12345.zip

| Power Plant Short Circuit Data | R (Ohm) | X (Ohm) |
| --- | --- | --- |
| SCR Normal |  |  |
| SCR Minimum |  |  |
| VCSCR |  |  |
| ESCR MV |  |  |

# Documentation

|  | Acceptance |
| --- | --- |
| - Model Documentation report |  |
| Version history |  |
| General Information |  |
| Overview |  |
| Parameters |  |
| Usage instructions |  |
| Functionalities |  |
| Supplementary documentation |  |

# Modelling

|  | Model complies (Yes/No) | Comments |
| --- | --- | --- |
| Aggregation |  |  |
| Aggregation (general aggregation and OHL/cable modelling) |  |  |
| Equipment |  |  |
| Transformer parameters and equipment (saturation, OLTC, grounding configuration, etc) |  |  |
| Compensation equipment, MOVs, filters etc. |  |  |
| House load |  |  |
| Control signals and parameters |  |  |
| “Static” control settings (not required to be adjustable in runtime, adjustment of any given setting must not require changes in more than one location) - Active power control settings (ramp rates, etc.) - Reactive power control settings (droop, deadband, etc.) - Frequency control (droop, deadband, frequency reference, etc.) - Fault current infeed settings - LVRT and OVRT settings - Protection settings |  |  |
| Runtime control signals and parameters (must be adjustable in runtime) - Available active power - Control mode activations for active, reactive and frequency control - Reference/setpoint changes for active, reactive and frequency control - All external references are adjustable as per unit values according to nominal active power and nominal voltage (cos(φ) for power factor control), where positive active and reactive power direction is defined from the plant towards the grid. |  |  |
| Monitoring signals |  |  |
| Relevant signals for unit and plant level controls - reference signals from plant controllers to individual units - unit level active and reactive current in positive and negative sequence - plant controller input measurements, AC voltage etc. - unit controller input measurements, AC voltage etc. incl. IBR internal control signals of Iq and Id) - PLL output signal (internal IBR signal) - Activation and deactivation of - fault current contribution - protection functions - limiters - status of converter blocking/de-blocking - generator RPM - Output of possible active damping function (e.g. SSO damping) |  |  |
| Model delivery format |  |  |
| model does not include any - global substitutions - radio links - multiple layers - PNI setups |  |  |
| The full plant model must be stored inside single main PSCAD module with just POC connection point and acceptable signal interfaces coming out |  |  |
| Main electrical circuit must be accessible down to LV terminals of individual units. Black-boxing only allowed for control and protection systems of individual active units such as IBR and PPC. |  |  |
| Real hardware code must be embedded in the model for all control and protection functions including signal processing, following the IEEE/CIGRE DLL standard |  |  |
| Model dependencies are placed in single sub-folder. No unnecessary or obsolete files shall be included. |  |  |
| Model does not include any .exe files |  |  |
| Model does not include any unnecessary or duplicate definitions or obsolete objects/component |  |  |
| Stage 2 update |  |  |
| (Only for Stage 2 models) Model corresponds to the final parametrisation of the facility after the VJV tests |  |  |

# Compatibility and usage

The following tests verify that the model includes all capabilities which are required for the model to work in all the use-cases where Fingrid will be using the model (and which are not tested already in the grid code functionalities part later)

| Test # | Test | Active power | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| C1 | Version compatibility | N/A | Model runs with PSCAD version, Fortran compiler and Visual Studio version specified by Fingrid | N/A | No errors with the specified version or compiler |  |  |
| C2 | Scaling and multiple instances | N/A | Model supports multiple (>50) instances in same simulation, with separate parametrization (inc. scaling) of different instances. | N/A | No errors with multiple instances, scaling or separate parametrization of different instances |  |  |
| C3 | Multiple run and snapshot features | N/A | Model supports multiple run and snapshot features | N/A | No errors with multiple run or snapshot features |  |  |
| C4 | Initialization | 1.0 | Flat run until model is in steady state | SCR Normal | Model initialized to steady state in less than 3 seconds |  |  |
| C5 | Compatibility with TSO system model | N/A | Model behaves as expected and runs without errors in TSO system model | N/A | No issues when integrating the model to the system level model |  |  |
| C6.1 | Runtime changes – available active power | N/A | Change available active power during the simulation | SCR Normal | Active power as expected |  |  |
| C6.2 | Runtime changes – active power / frequency control modes | 1.0 pu | Change control mode from active power control to frequency control. | SCR Normal | Active power to PCC is expected |  |  |
| C6.3 | Runtime changes – reactive power control modes | 1.0 pu | Change control mode from Vdroop -> Q-control -> PF-control. | SCR Normal | Reactive power to PCC is expected |  |  |

# Grid code functionalities

The following tests verify that the model works according to the corresponding grid code requirements. For BESS the tests are carried out for both production and demand mode, and in island operation test for different operating points according to SJV.

| Test # | Test | Active power/ Operating point | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| G1.1 | Setpoint change - voltage droop control | 1.0 pu | Setpoint change 1.0 pu -> 0.98 pu -> 1.0 pu -> 1.02 -> 1.0 pu | SCR Normal | Reactive power to PCC is expected with 4% droop |  |  |
| G1.2 | Setpoint change - Q-control | 1.0 pu | Setpoint change 0.0 pu -> -0.1 pu -> 0.0 pu -> 0.1 pu | SCR Normal | Reactive power to PCC is expected according to setpoint change |  |  |
| G1.3 | Setpoint change - pf-control | P ramp | Setpoint change 1.0 -> 0.98. After setpoint change P change 1.0 pu -> -1.0 pu -> 1.0 pu. | SCR Normal | Reactive power to PCC is expected according to setpoint change |  |  |
| G1.4 | Setpoint change - Active power max | P ramp | Setpoint change 1.0 pu -> 0.5 pu -> 1.0 pu | SCR Normal | Active power is expected according to setpoint change |  |  |
| G1.5 | Setpoint change - Active power min | P ramp | Setpoint change Pmin -> 0.5 pu -> Pmin | SCR Normal | Active power is expected according to setpoint change |  |  |
| G2.1 | Frequency sensitive mode | 0.5 pu and 0.1 pu | Frequency 50 Hz -> 49.5 Hz -> 50 Hz -> 50.5 Hz -> 50 Hz | SCR Normal | Active power follows frequency setpoints. Droop 2-12 %. |  |  |
| G2.2 | Limited frequency sensitive mode | 0.5 pu and 0.1 pu | Frequency 50 Hz -> 49 Hz -> 50 Hz -> 51 Hz -> 50 Hz | SCR Normal | Active power regulates as expected. Droop 4 %. |  |  |
| G3.1 | Operating limits - Voltage - Full power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G3.2 | Operating limits - Voltage - Partial power | 0.5 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G3.3 | Operating limits - Frequency - Full power | 1.0 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |
| G3.4 | Operating limits - Frequency - Partial power | 0.5 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |
| G4.1 | Reactive power capability - Full Power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power matches reactive power capacity calculations |  |  |
| G4.2 | Reactive power capability - Partial Power | 0.5 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power matches reactive power capacity calculations |  |  |
| G4.3 | Plant operating in momentary operating point 0.85 pu – Full power | 1.0 pu | PCC Voltage 1.0 pu -> 0.85 pu-> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power shall be produced for a minimum of 10 seconds. No tripping |  |  |
| G5.1 | Step response test | 1.0 pu | According to SJV2024 chapter 14.1.2 | VCSCR | Performance criteria from SJV2024 13.2.2. Reactive power to PCC matches droop setting. |  |  |
| G6.1.1 | Fault ride through – Disturbance 1 | 1.0 pu | SJV table 14.2, 3-ph SC | SCR normal after fault SCR minimum | No tripping, expected recovery according to SJV2024 |  |  |
| G6.1.2 | Fault ride through – Disturbance 4 | 1.0 pu | SJV table 14.2, 3-ph SC | SCR normal | No tripping, expected recovery according to SJV2024 |  |  |
| G6.1.3 | Fault ride through – Disturbance 2 | 1.0 pu | SJV table 14.2, 3-ph SC with vector shift +30° | SCR normal after fault SCR = max(ESCR HV, 2) | No tripping, expected recovery according to SJV2024 |  |  |
| G6.1.4 | Fault ride through – Disturbance 3 | 1.0 pu | SJV table 14.2, 3-ph SC with vector shift -30° | SCR normal after fault SCR = max(ESCR HV, 2) | No tripping, expected recovery according to SJV2024 |  |  |  |
| G6.1.5 | Fault ride through – Disturbance 1 | 1.0 pu | SJV table 14.2, 2-ph SC | SCR normal after fault SCR minimum | No tripping, expected recovery according to SJV2024 |  |  |
| G6.1.6 | Fault ride through – Disturbance 1 | 1.0 pu | SJV table 14.2, 2-ph SC to ground | SCR normal after fault SCR minimum | No tripping, expected recovery according to SJV2024 |  |  |
| G6.1.7 | Fault ride through – Disturbance 1 | 1.0 pu | SJV table 14.2, 1-ph ground fault | SCR normal after fault SCR minimum | No tripping, expected recovery according to SJV2024 |  |  |
| G6.1.8 | Fault ride through – Disturbance 1 | 1.0 pu | SJV table 14.2, 1-ph ground fault tested on all phases with U ≈ 0.6pu | SCR normal | No tripping, expected recovery according to SJV2024 |  |  |
| G6.2 | Overvoltage withstand capability | 1.0 pu | PCC Voltage 1.0 pu -> 1.2 pu-> 1.1 pu | Infinite bus - Forced voltage to PCC | No tripping, stable response according to SJV2024 |  |  |
| G6.3 | Multiple FRT | 1.0 pu | Fault and reconnection cycle. 3-ph SC. 100ms fault time @ T+0s, T+0.5s, T+1.0s, T+30.0s, T+35.0s | SCR Normal | Expected performance |  |  |
| G6.4.1 | Fault current injection – 3phg faults | 1.0 pu | Simulations with following PCC voltages: 1.2 pu, 1.1 pu, 0.9 pu, 0.8 pu, 0.7 pu, 0.6 pu, 0.5 pu, 0.4 pu, 0.3 pu, 0.2 pu, 0.1 pu, 0.0 pu. | SCR Normal | Active and reactive current provisions calculated. Reactive current shall be prioritized |  |  |
| G6.4.2 | Fault current injection – 2phg faults | 1.0 pu | Simulations with following PCC voltages: 1.2 pu, 1.1 pu, 0.9 pu, 0.8 pu, 0.7 pu, 0.6 pu, 0.5 pu, 0.4 pu, 0.3 pu, 0.2 pu, 0.1 pu, 0.0 pu. | SCR Normal | Active and reactive current provisions calculated. Reactive current shall be prioritized |  |  |
| G6.4.3 | Fault current injection – 1phg faults | 1.0 pu | Simulations with following PCC voltages: 1.2 pu, 1.1 pu, 0.9 pu, 0.8 pu, 0.7 pu, 0.6 pu, 0.5 pu, 0.4 pu, 0.3 pu, 0.2 pu, 0.1 pu, 0.0 pu. | SCR Normal | Active and reactive current provisions calculated. Reactive current shall be prioritized |  |  |
| G6.5 | Network vector shift | 0 and 1.0 pu | Vector shift +30° and -30° without fault and with SCR change, operation points A2, A4 and A5 | SCR normal after fault SCR = max(ESCR HV, 2) | No tripping, stable response, active power resists the vector shift |  |  |
| G6.6 | Island operation | a), b) and c) | According to SJV2024 chapter 14.1.4 | Special test network, see SJV2024 chapter 14.1.4 | Performance criteria from SJV2024 10.4.3 and 10.4.4 |  |  |
| G6.7 | Asymmetry balancing | - | Inject 3% voltage asymmetry to one phase | SCR normal | The power plant resists asymmetry |  |  |
| G6.8 | Impedance scan | - | Dynamic impedance scan from frequency range 1-300 Hz | Infinite bus | Performance criteria from SJV2024 10.4.3 and 10.4.4 |  |  |
| G7.1 | High voltage protection | 1.0 pu | Voltage raised until power plant trips | Infinite bus - Forced voltage to PCC | Power plant trips and user will be notified about the protective function. |  |  |
| G7.2 | Low voltage protection | 1.0 pu | Voltage lowered until power plant trips | Infinite bus - Forced voltage to PCC | Power plant trips and user will be notified about the protective function. |  |  |
| G7.3 | High frequency protection | 1.0 pu | Frequency raised until power plant trips | SCR Normal | Power plant trips and user will be notified about the protective function. |  |  |
| G7.4 | Low frequency protection | 1.0 pu | Frequency lowered until power plant trips | SCR Normal | Power plant trips and user will be notified about the protective function. |  |  |