PSS/E test template EXPIRED

# Documentation

|  | Requirement | Acceptance |
| --- | --- | --- |
| Documentation | PSS/E version compatibility |  |
|  | Usable time step |  |
|  | List of needed files |  |
|  | Minimum SCR |  |
|  | Model bandwidth and observable oscillation frequencies |  |
|  | Description of protection functions and signals |  |
|  | Description of possible POD or MSU |  |
|  | Instructions to change mode and setpoint |  |
|  | Instructions to bus number change |  |
|  | Full list of ICONs, CONs, STATEs, VARs and other parameters |  |

# Used SCR values

|  |  | R (Ohm) | X (Ohm) |
| --- | --- | --- | --- |
| Used SCR values | SCR Normal |  |  |
|  | SCR Minimum |  |  |
|  | VCSCR |  |  |

# Functionalities

|  | Number | Active power | Test | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Functionalities | 1.1 | 1.0 pu | Setpoint change - voltage droop control | Setpoint change 1.0 pu -> 0.98 pu -> 1.0 pu -> 1.02 -> 1.0 pu | SCR Normal | Reactive power to PCC is expected |  |  |
|  | 1.2 | 1.0 pu | Setpoint change - Q-control | Setpoint change 0.0 pu -> -0.1 pu -> 0.0 pu -> 0.1 pu | SCR Normal | Reactive power to PCC is expected |  |  |
|  | 1.3 | P ramp | Setpoint change - pf-control | Setpoint change 1.0 -> 0.98. After setpoint change P change 1.0 pu -> 0.8 pu -> 1.0 pu. | SCR Normal | Reactive power to PCC is expected |  |  |
|  | 1.4 | P ramp | Setpoint change - Active power max | Setpoint change 1.0 pu -> 0.5 pu -> 1.0 pu | SCR Normal | Active power is expected |  |  |
|  | 1.5 | P ramp | Setpoint change - Active power min | Setpoint change Pmin -> 0.5 pu -> Pmin | SCR Normal | Active power is expected |  |  |
|  | 2.1 | 0.5 pu | FSM | Frequency 50 Hz -> 49.5 Hz -> 50 Hz -> 50.5 Hz -> 50 Hz | SCR Normal | Active power follows frequency setpoints. Droop 2-12 %. |  |  |
|  | 2.2 | 0.5 pu | LFSM-O | Frequency 50 Hz -> 49 Hz -> 50 Hz -> 51 Hz -> 50 Hz | SCR Normal | Active power regulates as expected. Droop 2-12 %. |  |  |
| Capabilities | 3.1 | 1.0 pu | Operating limits - Voltage - Full power | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
|  | 3.2 | 0.5 pu | Operating limits - Voltage - Partial power | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
|  | 3.3 | 1.0 pu | Operating limits - Frequency - Full power | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |
|  | 3.4 | 0.5 pu | Operating limits - Frequency - Partial power | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |
|  | 4.1 | P ramp | Compensation equipment logic disconnect | Active power ramp 0.81 pu -> 0.19 pu | SCR normal | Compensation devices shall be connected at the beginning and shall be disconnected during the active power ramp |  |  |
|  | 4.2 | P ramp | Compensation equipment logic connect | Active power ramp 0.19 pu -> 0.81 pu | SCR normal | Compensation devices shall be disconnected at the beginning and shall be connected during the active power ramp |  |  |
|  | 5.1 | 1.0 pu | Reactive power capability - Full Power | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power matches reactive power capacity calculations |  |  |
|  | 5.2 | 1.0 pu | Plant operating in momentary operating point 0.85 pu – Full power | PCC Voltage 1.0 pu -> 0.85 pu-> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power shall be produced for a minimum of 10 seconds |  |  |
|  | 6.1 | 1.0 pu | Step response test - Full power | Background network voltage 1.0 pu -> 0.98 pu -> 1.0 pu -> 1.02 pu -> 1.0 pu. | VCSCR | Rise time for all steps 1.0±0.1 s. Reactive power to PCC matches droop setting. |  |  |
|  | 6.2 | 0.25 pu | Step response test 10 s - Full power | Background network voltage 1.0 pu -> 0.98 pu -> 1.0 pu -> 1.02 pu -> 1.0 pu. | VCSCR | Rise time for all steps 10 ± 1 s. Reactive power to PCC matches droop setting |  |  |
|  | 7.1.1 | 1.0 pu | Fault ride through test 1 - VJV | VJV table 10.1 or 10.2 test | SCR Normal, after fault SCR minimum | No tripping, expected recovery |  |  |
|  | 7.1.2 | 1.0 pu | Fault ride through test 2 - VJV | VJV table 10.1 or 10.2 test | SCR normal | No tripping, expected recovery |  |  |
|  | 7.2 | 1.0 pu | Multiple FRT | 10 consecutive 100 ms bolted three phase faults during same simulation | SCR Normal | Expected performance |  |  |
|  | 7.3 | 1.0 pu | Fault current injection | Fault sequence or separate simulations of three phase faults with following PPC residual voltages: 0.9 pu, 0.8 pu, 0.7 pu, 0.6 pu, 0.5 pu, 0.4 pu, 0.3 pu, 0.2 pu, 0.1 pu, 0.0 pu. | SCR Normal | Active and reactive current provisions calculated. Reactive power k-factor shall be as defined in VJV. Reactive current shall be prioritized. |  |  |
|  | 7.4 | 1.0 pu | LVRT | Fault sequence or separate simulations of PPC voltage drops | Infinite bus - Forced voltage to PCC/SCR Normal | LVRT activates and deactivates at expected thresholds. |  |  |
| Protections | 8.1 | 1.0 pu | High voltage protection | Voltage raised until power plant trips | Infinite bus - Forced voltage to PCC | Power plant trips and user will be notified about the protective function. |  |  |
|  | 8.2 | 1.0 pu | Low voltage protection | Voltage lowered until power plant trips | Infinite bus - Forced voltage to PCC | Power plant trips and user will be notified about the protective function. |  |  |
|  | 8.3 | 1.0 pu | High frequency protection | Frequency raised until power plant trips | SCR Normal | Power plant trips and user will be notified about the protective function. |  |  |
|  | 8.4 | 1.0 pu | Low frequency protection | Frequency lowered until power plant trips | SCR Normal | Power plant trips and user will be notified about the protective function. |  |  |
| PSS/E | A1 | 1.0 pu | Version compatibility 35 | Model run with different PSS/E 35 subversions | N/A | No errors with different subversions |  |  |
|  | A2 | - | Unique model name | Check that dynamic models have unique names | N/A | Dynamic model version number or other identifier included in the model name. This allows running different model versions in the same simulation |  |  |
|  | A3 | 1.0 pu | System decimal separator | Model run with different decimal separators | N/A | Model shall run regardless of system decimal separator |  |  |
|  | A4 | 1.0 pu | Initialization | Model run 5 minutes | N/A | Model initializes without changes in the model output and continues flat run for 5 minutes |  |  |