Fingrid PSS/E simulation model review report (Hybrid Power Plants)

Power Plant Name: 		Power Plant X

Connection Process Stage:	Stage 1(ION) /Stage 2(FON)

Model package:		Model_delivery_v_12345.zip

| Power Plant Short Circuit Data | R (Ohm) | X (Ohm) |
| --- | --- | --- |
| SCR Normal |  |  |
| SCR Minimum |  |  |
| VCSCR |  |  |
| ESCR MV |  |  |

# Documentation

|  | Model documentation complies (Yes/No) | Name of document and page number from where the needed item is documented |
| --- | --- | --- |
| - Model Documentation report |  |  |
| PSS/E version compatibility |  |  |
| Useable time step |  |  |
| List of needed files |  |  |
| Description of protection functions and signals |  |  |
| Description of possible POD or MSU |  |  |
| Instructions to change mode and setpoint |  |  |
| Instructions to bus number change |  |  |
| Full list of ICONs, CONs, STATEs, VARs and other relevant parameters with descriptions |  |  |
| Descriptions of ICONs, CONs, STATEs and VARs are available in PSS/E GUI (control flag MODE 8 is implemented) and they correspond with provided documentation descriptions |  | N/A |

# Grid code functionalities

The following tests verify that the model works according to the corresponding grid code requirements.

| Test # | Test | Active power | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| G1.1 | Setpoint change - voltage droop control | 1.0 pu | Setpoint change 1.0 pu -> 0.98 pu -> 1.0 pu -> 1.02 -> 1.0 pu | SCR Normal | Reactive power to PCC is expected with 4% droop |  |  |
| G1.2 | Setpoint change - Q-control | 1.0 pu | Setpoint change 0.0 pu -> -0.1 pu -> 0.0 pu -> 0.1 pu | SCR Normal | Reactive power to PCC is expected according to setpoint change |  |  |
| G1.3 | Setpoint change - pf-control | P ramp for BESS, other 1.0 pu | Setpoint change 1.0 -> 0.98. After setpoint change P change 1.0 pu -> -1.0 pu -> 1.0 pu. | SCR Normal | Reactive power to PCC is expected according to setpoint change |  | Only appelicable for hybrids with BESS |
| G2.1 | Frequency sensitive mode | BESS ± 0.1 pu, other 0.5 pu | Frequency 50 Hz -> 49.5 Hz -> 50 Hz -> 50.5 Hz -> 50 Hz | SCR Normal | Active power follows frequency setpoints. Droop 2-12 %. |  |  |
| G2.2 | Limited frequency sensitive mode | BESS ± 0.1 pu, other 0.5 pu | Frequency 50 Hz -> 49 Hz -> 50 Hz -> 51 Hz -> 50 Hz | SCR Normal | Active power regulates as expected. Droop 4 %. |  |  |
| G3.1 | Operating limits - Voltage - Full power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G3.2 | Operating limits - Voltage - Partial power | 0.5 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G3.3 | Operating limits - Frequency - Full power | 1.0 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |
| G3.4 | Operating limits - Frequency - Partial power | 0.5 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |
| G4.1 | Reactive power capability - Full Power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power matches reactive power capacity calculations |  |  |
| G4.2 | Reactive power capability - Partial Power | 0.5 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power matches reactive power capacity calculations |  |  |
| G4.3 | Plant operating in momentary operating point 0.85 pu – Full power | 1.0 pu | PCC Voltage 1.0 pu -> 0.85 pu-> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power shall be produced for a minimum of 10 seconds. No tripping |  |  |
| G5.1 | Step response test | 1.0 pu | According to SJV2024 chapter 14.1.2 | VCSCR | Performance criteria from SJV2024 13.2.2. Reactive power to PCC matches droop setting. |  |  |
| G6.1.1 | Fault ride through – Disturbance 1 | 1.0 pu | VJV table 10.3 or 10.4, 3-ph SC | SCR normal after fault SCR minimum | No tripping, expected recovery according to VJV2024 |  |  |
| G6.1.2 | Fault ride through – Disturbance 2 | 1.0 pu | VJV table 10.3 or 10.4, 3-ph SC | SCR Normal | No tripping, expected recovery according to VJV2024 |  |  |
| G6.1.3 | Fault ride through – Disturbance 3 | 1.0 pu | SJV table 14.2, 3-ph SC | SCR normal after fault SCR minimum | No tripping, expected recovery according to SJV2024 |  |  |
| G6.2 | Multiple FRT | 1.0 pu | Fault and reconnection cycle. 3-ph SC. 100ms fault time @ T+0s, T+0.5s, T+1.0s, T+30.0s, T+35.0s | SCR Normal | Expected performance |  |  |
| G6.3 | Overvoltage withstand capability | 1.0 pu | PCC Voltage 1.0 pu -> 1.2 pu-> 1.1 pu | Infinite bus - Forced voltage to PCC | No tripping, stable response according to VJV2024 |  |  |
| G6.4 | Network vector shift | 0 and 1.0 pu | Vector shift +30° and -30° without fault and with SCR change, operation points A2, A4 and A5 | SCR normal after fault SCR = max(ESCR HV, 2) | No tripping, stable response, active power resists the vector shift |  |  |
| A1 | Version compatibility | 1.0 pu | Model run with different PSS/E 36 subversions | N/A | No errors with different subversions. |  |  |
| A2 | Unique model name |  | Check that dynamic models have unique names | N/A | Dynamic model version number or other identifier included in the model name. This allows running different model versions in the same simulation |  |  |
| A3 | System decimal separator | 1.0 pu | Model run with different decimal separators | N/A | Model should run regardless of system decimal separator |  |  |
| A4 | Initialization | 1.0 pu | Model run 5 minutes | N/A | Model initializes without changes in the model output and continues flat run for 5 minutes |  |  |
| A5 | Implementation of control flag MODE 6 (activity DYDA) |  | Save snapshot data as DYR file | N/A | The model writes its input data correctly in a DYR file |  |  |
| A6 | (Only for FON stage models) Model corresponds to the final parametrisation of the facility after the SJV tests |  |  |  |  |  |  |