Fingrid PSS/E simulation model review report (KJV2018)

Demand Facility Name: 		Data Center X

Connection Process Stage:	Stage 1 (ION) /Stage 2 (FON)

Model package:		Model_delivery_v_12345.zip

| Facility Short Circuit Data | R (Ohm) | X (Ohm) |
| --- | --- | --- |
| SCR Normal |  |  |
| SCR Minimum |  |  |

| Power data | P (MW) |
| --- | --- |
| Maximum active power Pmax (1.0 pu) |  |

# Documentation

|  | Model documentation complies (Yes/No) | Name of document and page number from where the needed item is documented |
| --- | --- | --- |
| PSS/E version compatibility |  |  |
| Useable time step |  |  |
| List of needed files |  |  |
| Description of protection functions and signals |  |  |
| Instructions to bus number change |  |  |
| Full list of ICONs, CONs, STATEs, VARs and other relevant parameters are provided in documentation |  |  |
| Descriptions of ICONs, CONs, STATEs and VARs are available in PSS/E GUI (control flag MODE 8 is implemented) and they correspond with provided documentation descriptions |  | N/A |

# Compatibility and usage

The following tests verify that the model includes all capabilities which are required for the model to work in all the use-cases where Fingrid will be using the model (and which are not tested already in the grid code functionalities part later)

| Test # | Test | Active power/ Operating point | Description | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| A1 | Version compatibility | 1.0 pu | Model run with different PSS/E 36 subversions | No errors with different subversions. |  |  |
| A2 | Unique model name |  | Check that dynamic models have unique names | Dynamic model version number or other identifier included in the model name. This allows running different model versions in the same simulation |  |  |
| A4 | Initialization | 1.0 pu | Model run 5 minutes | Model initializes without changes in the model output and continues flat run for 5 minutes |  |  |
| A5 | Implementation of control flag MODE 6 (activity DYDA) |  | Save snapshot data as DYR file | The model writes its input data correctly in a DYR file |  |  |
| A6 | (Only for stage 2 models) Model corresponds to the final parametrisation of the facility after the KJV tests |  |  |  |  |  |

# Grid code functionalities

The following tests verify that the model works according to the corresponding grid code requirements.

| Test # | Test | Active power | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| G1.1 | Operating limits - Voltage - Full power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G1.2 | Operating limits - Voltage - Partial power | 0.2 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation |  |  |
| G1.3 | Operating limits - Frequency - Full power – UFLS enabled | 1.0 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz, Rate of change 2 Hz/s. UFSL enabled. | SCR Normal | Expected response |  |  |
| G1.4 | Operating limits - Frequency - Full power – UFLS disabled | 1.0 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz, Rate of change 2 Hz/s. UFLS disabled | SCR Normal | Expected response |  |  |
| G2.1 | Step change in frequency | 1.0 pu | Frequency 50 Hz -> 49 Hz -> 50 Hz -> 51 Hz -> 50 Hz. Rate of change 2 Hz/s. | SCR Normal | Expected response |  |  |
| G3.1 | Current limiter activation | 1.0 pu | Ramp voltage down to current limitation activation threshold and then back up to 100 % | SCR normal | Expected results |  |  |
| G3.2 | Current blocking activation | 1.0 pu | Ramp voltage down to current block activation threshold without causing a trip and then back up to 100 % | SCR normal | Expected results |  |  |
| G4.1.1 | Fault ride through – and post-fault active power recovery | 1.0 pu | 3-ph SC with 200 ms fault time | SCR normal, after fault SCR minimum | Expected results |  |  |
| G4.1.2 | Fault ride through – and post-fault active power recovery | 1.0 pu | 3-ph SC with 200 ms fault time and with residual voltage U = 0.25 pu | SCR Normal | Expected results |  |  |
| G4.2 | Overvoltage withstand capability | 1.0 pu and 0.2 pu | PCC Voltage 1.0 pu -> 1.2 (5 s.) pu-> 1.1 pu | Infinite bus - Forced voltage to PCC | Expected results |  |  |
| G4.3 | Multiple FRT 1 | 1.0 pu | Fault and reconnection cycle. 3-ph SC. 100 ms fault time @ T+0 s, T+0.5 s, T+1.0 s, T+30.0 s, T+35.0 s | SCR Normal | Expected results |  |  |
| G4.4 | Multiple FRT 2 | 1.0 pu | Fault and reconnection cycle. 10 consecutive 100 ms bolted 3-ph SC during same simulation. 5 second intervals. | SCR Normal | Expected results |  |  |
| G4.5 | Switchover to high voltage backup supply (if applicable) | 1.0 pu | Switchover to external high voltage backup connection (for example from 400 kV to 110 kV backup supply) | SCR Normal | Expected results |  |  |
| G5.1 | High voltage protection | 1.0 pu | Voltage raised until demand facility trips | Infinite bus - Forced voltage to PCC | Demand facility trips and user will be notified about the protective function. |  |  |
| G5.2 | Low voltage protection | 1.0 pu | Voltage lowered until demand facility trips | Infinite bus - Forced voltage to PCC | Demand facility trips and user will be notified about the protective function. |  |  |
| G5.3 | High frequency protection | 1.0 pu | Frequency raised until demand facility trips | SCR Normal | Demand facility trips and user will be notified about the protective function. |  |  |
| G5.4 | Low frequency protection | 1.0 pu | Frequency lowered until demand facility trips | SCR Normal | Demand facility trips and user will be notified about the protective function. |  |  |