Fingrid PSS/E simulation model review report (SJV2024)

Power Plant Name: 		Power Plant X

Connection Process Stage:	Stage 1 (ION) /Stage 2 (FON)

Model package:		Model_delivery_v_12345.zip

| Power Plant Short Circuit Data | R (Ohm) | X (Ohm) |
| --- | --- | --- |
| SCR Normal |  |  |
| SCR Minimum |  |  |
| VCSCR |  |  |
| ESCR MV |  |  |

# Documentation

|  | Model documentation complies (Yes/No) | Name of document and page number from where the needed item is documented |
| --- | --- | --- |
| - Model Documentation report |  |  |
| PSS/E version compatibility |  |  |
| Useable time step |  |  |
| List of needed files |  |  |
| Description of protection functions and signals |  |  |
| Description of possible POD or MSU |  |  |
| Instructions to change mode and setpoint |  |  |
| Instructions to bus number change |  |  |
| Full list of ICONs, CONs, STATEs, VARs and other relevant parameters with descriptions |  |  |
| Descriptions of ICONs, CONs, STATEs and VARs are available in PSS/E GUI (control flag MODE 8 is implemented) and they correspond with provided documentation descriptions |  | N/A |

# Grid code functionalities

The following tests verify that the model works according to the corresponding grid code requirements. For BESS the tests are carried out for both production and demand mode, and in island operation test for different operating points according to SJV.

| Test # | Test | Active power/ Operating point | Description | Background network | Acceptance criteria | Model complies (Yes/No) | Comments |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G1.1 | Setpoint change - voltage droop control | 1.0 pu | Setpoint change 1.0 pu -> 0.98 pu -> 1.0 pu -> 1.02 -> 1.0 pu | SCR Normal | Reactive power to PCC is expected with 4 % droop |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G1.2 | Setpoint change - Q-control | 1.0 pu | Setpoint change 0.0 pu -> -0.1 pu -> 0.0 pu -> 0.1 pu | SCR Normal | Reactive power to PCC is expected according to setpoint change |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G1.3 | Setpoint change - pf-control | P ramp | Setpoint change 1.0 -> 0.98. After setpoint change P change 1.0 pu -> -1.0 pu -> 1.0 pu. | SCR Normal | Reactive power to PCC is expected according to setpoint change |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G1.4 | Setpoint change - Active power max | P ramp | Setpoint change 1.0 pu -> 0.5 pu -> 1.0 pu | SCR Normal | Active power is expected according to setpoint change |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G1.5 | Setpoint change - Active power min | P ramp | Setpoint change Pmin -> 0.5 pu -> Pmin | SCR Normal | Active power is expected according to setpoint change |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G2.1 | Frequency sensitive mode | 0.5 pu and 0.1 pu | Frequency 50 Hz -> 49.5 Hz -> 50 Hz -> 50.5 Hz -> 50 Hz | SCR Normal | Active power follows frequency setpoints. Droop 2-12 %. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G2.2 | Limited frequency sensitive mode | 0.5 pu and 0.1 pu | Frequency 50 Hz -> 49 Hz -> 50 Hz -> 51 Hz -> 50 Hz | SCR Normal | Active power regulates as expected. Droop 4 %. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G3.1 | Operating limits - Voltage - Full power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G3.2 | Operating limits - Voltage - Partial power | 0.5 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu. | Infinite bus - Forced voltage to PCC | Stable operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G3.3 | Operating limits - Frequency - Full power | 1.0 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G3.4 | Operating limits - Frequency - Partial power | 0.5 pu | Frequency 50 Hz -> 47.5 Hz -> 50 Hz -> 51.5 Hz -> 50 Hz | SCR Normal | Stable operation. Active power reduction is not more than 10 % per 1 Hz when frequency is below 49.0 Hz |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G4.1 | Reactive power capability - Full Power | 1.0 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power matches reactive power capacity calculations |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G4.2 | Reactive power capability - Partial Power | 0.5 pu | PCC voltage 1.0 pu -> 0.9 pu -> 1.0 pu -> 1.1 pu -> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power matches reactive power capacity calculations |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G4.3 | Plant operating in momentary operating point 0.85 pu – Full power | 1.0 pu | PCC Voltage 1.0 pu -> 0.85 pu-> 1.0 pu | Infinite bus - Forced voltage to PCC | Reactive power shall be produced for a minimum of 10 seconds. No tripping. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G5.1 | Step response test | A4 and A5 | According to SJV2024 chapter 14.1.2 | VCSCR | Performance criteria from SJV2024 13.2.2. Reactive power to PCC matches droop setting. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.1.1 | Fault ride through –Disturbance 1 | 1.0 pu | SJV table 14.2, 3-ph SC | SCR normal after fault SCR minimum | No tripping, expected recovery according to SJV2024 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.1.2 | Fault ride through – Disturbance 4 | 1.0 pu | SJV table 14.2, 3-ph SC | SCR normal | No tripping, expected recovery according to SJV2024 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.1.3 | Fault ride through –Disturbance 2 | 1.0 pu | SJV table 14.2, 3-ph SC with vector shift +30° | SCR normal after fault SCR = max(ESCR HV, 2) | No tripping, expected recovery according to SJV2024 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.1.4 | Fault ride through –Disturbance 3 | 1.0 pu | SJV table 14.2, 3-ph SC with vector shift -30° | SCR normal after fault SCR = max(ESCR HV, 2) | No tripping, expected recovery according to SJV2024 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.2 | Overvoltage withstand capability | 1.0 pu | PCC Voltage 1.0 pu -> 1.2 pu-> 1.1 pu | Infinite bus - Forced voltage to PCC | No tripping, stable response according to SJV2024 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.3 | Multiple FRT | 1.0 pu | Fault and reconnection cycle. 3-ph SC. 100ms fault time @ T+0s, T+0.5s, T+1.0s, T+30.0s, T+35.0s | SCR Normal | Expected performance |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.4.1 | Fault current injection – 3phg faults | 1.0 pu | Simulations with following PCC voltages: 1.2 pu, 1.1 pu, 0.9 pu, 0.8 pu, 0.7 pu, 0.6 pu, 0.5 pu, 0.4 pu, 0.3 pu, 0.2 pu, 0.1 pu, 0.0 pu. | SCR Normal | Active and reactive current provisions calculated. Reactive current shall be prioritized |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.5 | Network vector shift | 0 and 1.0 pu | Vector shift +30° and -30° without fault and with SCR change, operation points A2, A4 and A5 | SCR normal after fault SCR = max(ESCR HV, 2) | No tripping, stable response, active power resists the vector shift |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G6.6 | Island operation | a), b) and c) | According to SJV2024 chapter 14.1.4 | Special test network, see SJV2024 chapter 14.1.4 | Performance criteria from SJV2024 10.4.3 and 10.4.4 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G7.1 | High voltage protection | 1.0 pu | Voltage raised until power plant trips | Infinite bus - Forced voltage to PCC | Power plant trips and user will be notified about the protective function. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G7.2 | Low voltage protection | 1.0 pu | Voltage lowered until power plant trips | Infinite bus - Forced voltage to PCC | Power plant trips and user will be notified about the protective function. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G7.3 | High frequency protection | 1.0 pu | Frequency raised until power plant trips | SCR Normal | Power plant trips and user will be notified about the protective function. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G.7.4 | Low frequency protection | 1.0 pu | Frequency lowered until power plant trips | SCR Normal | Power plant trips and user will be notified about the protective function. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A1 | Version compatibility | 1.0 pu | Model run with different PSS/E 36 subversions | N/A | No errors with different subversions. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A2 | Unique model name |  | Check that dynamic models have unique names | N/A | Dynamic model version number or other identifier included in the model name. This allows running different model versions in the same simulation |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A3 | System decimal separator | 1.0 pu | Model run with different decimal separators | N/A | Model should run regardless of system decimal separator |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A4 | Initialization | 1.0 pu | Model run 5 minutes | N/A | Model initializes without changes in the model output and continues flat run for 5 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A5 | Implementation of control flag MODE 6 (activity DYDA) |  | Save snapshot data as DYR file | N/A | The model writes its input data correctly in a DYR file |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A6 | (Only for FON stage models) Model corresponds to the final parametrisation of the facility after the SJV tests |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |