## Taulukko 7.1
1 | Yleistiedot |  |  | Viite
| 1.1 | Sähköpääkaavio (single line diagram)
| 1.2 | Sähkövaraston tyyppi (esim. sähköakku, polttokenno tms.)
| 1.3 | Sijaintitieto (paikkakunta, alue, liittymispiste, koordinaatit)
| 1.4 | Tietoliikenneyhteyksien yhteyskaavio (CSA, Common Service Architecture) ja tietoturvasuunnitelma
2 | Muuntajien tekniset tiedot:
| 2.1 | Sähkövaraston muuntajien lukumäärä, toimittaja- ja tyyppitiedot
| 2.2 | Muuntajien dokumentaatio ja datalehdet
Teho [MVA], virta [A], muuntosuhde [ensiö/toisio], oikosulkuimpedanssi [%], oikosulkuresistanssi [%], kytkentäryhmä ja maadoitustiedot, käämikytkimen säätöalue ja askel [%,%], käämikytkimen askeleiden määrä ja valittu askel [kpl, askel]
3 | Sähkövaraston tekniset tiedot:
| 3.1 | Sähkövarastointiyksiköiden lukumäärä, toimittaja- ja tyyppitiedot
| 3.2 | Sähkövarastointiyksiköiden dokumentaatio ja datalehdet
Mitoitusteho kulutustilassa [MW], mitoitusteho tuotantotilassa [MW], virta [A], jännite [V]
| 3.3 | Tuotanto- ja kulutustehon riippuvuus käyttöolosuhteista (esim. lämpötila)
| 3.4 | Mahdollisesti käytössä olevat kompensointi- ja/tai tehokertoimen korjaamisessa käytettävät laitteet
Lukumäärä, tyyppi, mitoitusarvot (teho, virta, jännite, taajuus)
Mikäli hyödynnetään yliaaltojen suodatukseen, tiedot rakenteesta ja viritystaajuudesta
4 | Sähkövaraston järjestelmätekniset ominaisuudet:
Seuraavat kohdat voidaan korvata esim. valmistajan laitedokumenteilla tai muulla testausdokumentaatiolla
| 4.1 | Sähkövaraston loistehokapasiteetti ja yksittäisten yksiköiden loistehokapasiteetit
| 4.2 | Sähkövaraston kyky toimia ali- ja ylijännitteellä
| 4.3 | Sähkövaraston kyky toimia ali- ja ylitaajuudella
| 4.4 | Sähkövaraston taajuuden muutosnopeuden sietokyky
| 4.5 | Sähkövaraston lähivika- ja ylijännitekestoisuus
| 4.6 | Sähkövaraston loisvirran syöttö jännitehäiriön ja ylijännitteen aikana
| 4.7 | Sähkövaraston pätötehonsäätöominaisuudet
| 4.8 | Sähkövaraston jännitteensäätöominaisuudet
5 | Sähkövaraston suojaustiedot:
| 5.1 | Sähkövaraston relesuojauskaavio
| 5.2 | Sähkövaraston lopulliset relesuojausasettelut
| 5.3 | Tiedot saarekesuojan toimintaperiaatteesta (jos käytössä)
6 | Käyttöönottodokumentit:
| 6.1 | Käyttöönottopöytäkirjat
| 6.2 | Jännitteensäädön lopulliset asetteluarvot ja toimintatila
Vaatimustenmukaisuusilmoitus
Liittyjän edustaja vahvistaa allekirjoituksellaan, että tämän taulukon viitetietojen osoittamat dokumentit todentavat sähkövaraston täyttävän sille asetetut Vaatimukset. Paikka, aika, allekirjoitus ja nimenselvennys:

## Taulukko 7.1 EN
1 | General data |  |  | Ref
| 1.1 | Single line diagram
| 1.2 | Type of the grid energy storage system (e.g. battery, fuel cell etc.)
| 1.3 | Location data (municipality, area, connection point, coordinates)
| 1.4 | Diagram of common service architecture (CSA) and information security plan
2 | Technical details of transformers:
| 2.1 | Number, supplier and type details of the grid energy storage system’s transformers
| 2.2 | Documentation and data sheets of transformers
Power [MVA], current [A], transformation ratio [primary/secondary], short-circuit impedance [%], short-circuit resistance [%], vector group and earthing details, control range and step of on- or off-load tap-changer [%, %], number of steps of on- or off-load tap-changer and selected step [quantity, step]
3 | Technical details of grid energy storage system:
| 3.1 | Number, supplier and type details of grid energy storage system units
| 3.2 | Documentation and data sheets of grid energy storage system units
Rated capacity in demand mode [MW], rated capacity in production mode [MW], current [A], voltage [V]
| 3.3 | Dependence of production and demand power on operating conditions (e.g. temperature)
| 3.4 | Potentially used compensation devices and/or devices used for the correction of power factor
Number, type, rated values of devices (power, current, voltage, frequency)
If used for the filtering of harmonics, data on the structure and tuning frequency
4 | Grid energy storage system's operational characteristics:
The following items may be replaced, for example, by the manufacturer's device documents or other testing documentation
| 4.1 | Reactive power capacity of the grid energy storage system and units
| 4.2 | Ability to operate at undervoltage and overvoltage
| 4.3 | Ability to operate at underfrequency and overfrequency
| 4.4 | Rate of change of frequency withstand capability
| 4.5 | Fault-ride-through capability
| 4.6 | Reactive current injection during a voltage disturbance
| 4.7 | Active power control characteristics
| 4.8 | Voltage control characteristics
5 | Protection details of the grid energy storage system:
| 5.1 | Relay protection diagram of the grid energy storage system
| 5.2 | Final relay protection setpoints
| 5.3 | Data on the operating principle of island protection (if used)
6 | Commissioning documents:
| 6.1 | Commissioning records
| 6.2 | Final setpoint values and mode of voltage control
Statement of compliance
The grid energy storage system owner’s representative confirms with a signature that the documents referred to in this table’s reference details prove that the grid energy storage system meets the Specifications set for it. Place, date, signature and printed name:

## Taulukko 7.2
| Vaihe 1 (Suunnittelu) |  | Viite
1 | Yleistiedot
1.1 | Hankkeen nimi ja yhteystiedot, liittymispiste, liittymispisteen verkonhaltija ja yhteystiedot
1.2 | Sähköpääkaavio (single line diagram)
Sähkövaraston pääkomponentit ja niitä yhdistävä sähköverkko
Pääkaaviossa esitettyjen komponenttien ja johdinten sähköiset parametrit
1.3 | Sähkövaraston tyyppi (esim. sähköakku, polttokenno tms.)
1.4 | Sijaintitieto (paikkakunta, alue, liittymispiste, koordinaatit)
1.5 | Tietoliikenneyhteyksien yhteyskaavio (CSA, Common Service Architecture) ja tietoturvasuunnitelma (luku 10.3.7)
2 | Tekniset tiedot
2.1 | Sähkövarastointiyksiköiden lukumäärä, toimittaja- ja tyyppitiedot
2.2 | Sähkövarastointiyksiköiden dokumentaatio ja datalehdet
Mitoitusteho kulutustilassa [MW], mitoitusteho tuotantotilassa [MW], virta [A], jännite [V]
2.3 | Muuntajien dokumentaatio ja datalehdet
Teho [MVA], virta [A], muuntosuhde [ensiö/toisio], oikosulkuimpedanssi [%], oikosulkuresistanssi [%], kytkentäryhmä ja maadoitustiedot, käämikytkimen säätöalue ja askel [%,%], käämikytkimen askeleiden määrä ja valittu askel [kpl, askel]
2.4 | Muiden komponenttien dokumentaatio ja datalehdet
Soveltuvin osin vastaavat tiedot kuin sähkövarastointiyksiköistä (kohta 2.2) ja muuntajista (kohta 2.3) sekä kaikki ne tiedot, joilla on merkitystä Vaatimusten kannalta (esim. rakenne, suodattimen viritystaajuus)
3 | Jännite-taajuus toiminta-alue
3.1 | Sähkövaraston kyky toimia ali- ja ylijännitteellä (luku 10.2.1 tai 10.5.2)
3.2 | Sähkövaraston kyky toimia ali- ja ylitaajuudella (luku 10.2.1 tai 10.5.2)
3.3 | Sähkövaraston taajuuden muutosnopeuden sietokyky (luku 10.2.2)
4 | Lähivika- ja ylijännitekestoisuus
4.1 | Tiedot ja tarkastelu toiminnasta jännitehäiriön aikana ja mahdolliset tehdaskokeiden raportit (luku 10.3.2 tai 10.5.3,luku 14.1.1)
4.2 | Tiedot toiminnasta lyhytaikaisen ylijännitteen aikana ja mahdolliset tehdaskokeiden raportit (luku 10.3.3)
4.3 | Tiedot pätötehon palautumisesta jännitehäiriön jälkeen (luku 10.3.5)
5 | Verkkoa luovat ominaisuudet
5.1 | Dokumentaatio ja kuvaus verkkoa luovista säätöominaisuuksista (luku 10.4.3)
Dokumentaatio säätöjärjestelmän toteutuksesta ja teknisista ominaisuuksista.
Siirtofunktioina kuvattu toiminnallinen lohkokaavioesitys säädön toteutuksesta.
5.2 | Tarkastelut toiminnasta saarekekäytössä ja verkon kulmamuutoksessa sekä impedanssiskannaus (luku 14.1.3, 14.1.4 ja 14.1.5)
5.3 | Säätäjille aseteltavat parametrit ja toimintaviiveet
6 | Pätötehon ja taajuuden säätö
6.1 | Dokumentaatio ja kuvaus pätötehon ja taajuuden säädöstä (luku 11)
Dokumentaatio säätöjärjestelmän toteutuksesta ja teknisista ominaisuuksista.
Siirtofunktioina kuvattu toiminnallinen lohkokaavioesitys säädön toteutuksesta.
6.2 | Säätäjille aseteltavat parametrit ja toimintaviiveet
7 | Omakäyttö sekä tuotanto- ja kulutustehon muutokset
7.1 | Tiedot sähkövaraston toiminnasta omakäytöllä (luku 11.3.2)
Sähkövaraston omakäyttötehon suuruus
7.2 | Tuotanto- ja kulutustehon muutokset
Pätötehon muutokset taajuus- ja jännitevaihteluiden yhteydessä
Pätötehon riippuvuus käyttöolosuhteista (esim. lämpötila)
Pätötehon muutosnopeus, muutosnopeuden rajoittimien toiminnallisuus sekä rajoitteet
8 | Sähkövaraston loistehokapasiteetti
8.1 | Loistehokapasiteettilaskelma (luku 12.2.4)
8.2 | PQ-diagammit
Sähkövarastointiyksiköiden PQ-diagammit sekä tiedot niiden jännite-taajuusriippuvuudesta. PQ-diagrammeihin tulee merkitä loistehoa rajoittavien rajoittimien asettelut.
8.3 | Muut loistehoon vaikuttavat komponentit
Loistehoa tuottavat (esim. kondensaattori tai STATCOM) ja kuluttavat komponentit sekä niiden toiminta komponentteihin vaikuttavien suureiden (esim. jännite, pätöteho) funktiona
9 | Jännitteen ja loistehon säätö
9.1 | Dokumentaatio ja kuvaus jännitteen ja loistehon säädöstä (luku 13)
Dokumentaatio säätöjärjestelmän toteutuksesta ja teknisista ominaisuuksista.
Siirtofunktioina kuvattu toiminnallinen lohkokaavioesitys säädön toteutuksesta.
9.2 | Säätäjille aseteltavat parametrit ja toimintaviiveet
9.3 | Jännitteensäädön suorituskykylaskelma (luku 14.1.2)
10 | Sähkövaraston suojausasettelut ja vaikutus sähkön laatuun
10.1 | Suojausasettelut (luku 10.3.6)
Sähkövaraston relesuojauskaavio ja asettelut.
10.2 | Sähkövaraston vaikutus sähkön laatuun (luku 10.4.5)
Sähkövaraston vaikutus sähkön laatuun sekä mahdolliset tehdaskokeiden raportit.
11 | Dynaamisen toiminnan laskentaan tarvittavat tiedot
Projektikohtaiset dynaamisen toiminnan mallintamiseen tarvittavat tiedot tai laskentamallit Vaatimusten mukaisesti (luku 16)
12 | Reaaliaikaiset mittaustiedot ja instrumentointi
12.1 | Reaaliaikaisten mittaustietojen toimitustapa ja todennus (luku 9.2 ja 10.4.1)
12.2 | Tallentimien tekniset tiedot ja asettelut (luku 9.3 tai 9.4)
13 | Erityistarkasteluvaatimukset
Vaadittavat erityistarkastelut Vaatimuksiin liittyen (luku 5)
14 | Projektin aikataulu ja käyttöönotto
Sähkövarastohankkeen aikataulu ja Vaatimuksiin liittyvien käyttöönottokokeiden suunniteltu ajankohta.
Vaatimustenmukaisuusilmoitus
Liittyjän edustaja vahvistaa allekirjoituksellaan, että tämän taulukon viitetietojen osoittamat dokumentit todentavat sähkövaraston täyttävän sille asetetut Vaatimukset. Paikka, aika, allekirjoitus ja nimenselvennys:

## Taulukko 7.2 EN
| Stage 1 (Planning) |  | Ref
1 | General data
1.1 | Name and contact details of project, connection point, relevant network operator and contact details
1.2 | Single line diagram
The main components of the grid energy storage system and the electricity network that connects the components
Electric parameters of the components and conductors presented in the single line diagram
1.3 | Type of the grid energy storage system (e.g. battery, fuel cell etc.)
1.4 | Location data (municipality, area, connection point, coordinates)
1.5 | Diagram of common service architecture (CSA) and information security plan (section 10.3.7)
2 | Technical data
2.1 | Number, supplier and type details of grid energy storage system units
2.2 | Documentation and data sheets of the grid energy storage system units
Rated capacity in demand mode [MW], rated capacity in production mode [MW], current [A], voltage [V]
2.3 | Documentation and data sheets of transformers
Power [MVA], current [A], transformation ratio [primary/secondary], short-circuit impedance [%], short-circuit resistance [%], vector group and earthing details, control range and step of on- or off-load tap-changer [%, %], number of steps of on- or off-load tap-changer and selected step [quantity, step]
2.4 | Documentation and data sheets of other components
Where applicable, the same data as on grid energy storage system units (section 2.2) and transformers (section 2.3) as well as all data that is relevant in terms of the Specifications (e.g. structure, filter tuning frequency)
3 | Operating voltage and frequency range
3.1 | Ability to operate at undervoltage and overvoltage (section 10.2.1 or 10.5.2)
3.2 | Ability to operate at underfrequency and overfrequency (section 10.2.1 or 10.5.2)
3.3 | Rate of change of frequency withstand capability (section 10.2.2)
4 | Fault-ride-through capability
4.1 | Data and calculation of the operation of the grid energy storage system during voltage disturbance, and potential reports on factory testing (section 10.3.2 or 10.5.3, section 14.1.1)
4.2 | Data on capability to operate during short-time overvoltage and potential reports on factory testing (section 10.3.3)
4.3 | Data on active power recovery after a voltage disturbance (section 10.3.5)
5 | Grid-forming characteristics
5.1 | Documentation and description of grid-forming control features (section 10.4.3)
Documentation on the control system’s implementation and technical characteristics.
Functional block diagram on the implementation of control described as transfer curves.
5.2 | Study of operation in island operation and in the event of a network vector shift, and a impedance scan (section 14.1.3, 14.1.4 and 14.1.5)
5.3 | Parameters and operating delays set for controllers
6 | Active power control and frequency control
6.1 | Documentation and description of active power control and frequency control (chapter 11)
Documentation on the control system’s implementation and technical characteristics.
Functional block diagram on the implementation of control described as transfer curves.
6.2 | Parameters and operating delays set for controllers
7 | House load and changes in production and demand power
7.1 | Data on the operation of the grid energy storage system in house load operation (section 11.3.2)
Magnitude of house load of the grid energy storage system
7.2 | Changes in production and demand power
Changes in active power in conjunction with frequency and voltage fluctuations
Dependence of active power on operating conditions (e.g. temperature)
Rate of change of active power, functionality and constraints of limiters of rate of change
8 | Reactive power capacity of the grid energy storage system
8.1 | Reactive power capacity calculation (section 12.2.4)
8.2 | PQ diagrams
PQ diagrams of grid energy storage system units and data on their voltage-frequency dependence. The setpoints used in the reactive power limiters shall be specified in the PQ diagrams.
8.3 | Other components influencing reactive power
Components that generate (e.g. capacitor or STATCOM) and consume reactive power, and their operation as a function of the variables (e.g. voltage, active power) influencing the components
9 | Voltage control and reactive power control
9.1 | Documentation and description of voltage control and reactive power control (chapter 13)
Documentation on the control system’s implementation and technical characteristics.
Functional block diagram on the implementation of control described as transfer curves.
9.2 | Parameters and operating delays set for controllers
9.3 | Voltage control performance calculation (section 14.1.2)
10 | Protection setpoints of the grid energy storage system and impact on power quality
10.1 | Protection setpoints (section 10.3.6)
Relay protection diagram of the grid energy storage system and the setpoints of the described protection.
10.2 | The grid energy storage system’s impact on power quality (section 10.4.5)
Description of the grid energy storage system impact on power quality and potential reports of factory testing.
11 | Data required for dynamic modelling
Project-specific data or simulation models required by the modelling of dynamic operation in accordance with the Specifications (chapter 16)
12 | Real-time measurement data and instrumentation
12.1 | Method of delivery and verification of real-time measurement data (section 9.2 and 10.4.1)
12.2 | Technical data on and the setpoints of disturbance and swing recorders (section 9.3 or 9.4)
13 | Specific study requirements
Required specific studies related to the Specifications (chapter 5)
14 | Project’s schedule and commissioning
Schedule of the grid energy storage system project and the planned timing of the commissioning tests relating to the Specifications.
Statement of compliance
The grid energy storage system owner’s representative confirms with a signature that the documents referred to in this table’s reference details prove that the grid energy storage system meets the Specifications set for it. Place, date, signature and printed name:

## Taulukko 7.3
| Vaihe 2 (Käyttöönotto ja todentaminen) |  | Viite
1 | Muutokset ja täsmennykset
Muutokset ja täsmennykset todentamisprosessin vaiheessa 1 toimitettuihin tietoihin
2 | Käyttöönottokokeisiin liittyvät tiedot
2.1 | Käyttöönottokoesuunnitelma (luku 15.3.1)
Yksityiskohtainen käyttöönottokoesuunnitelma, sähkövarastotoimittajan antamat käyttöönotto-ohjeet ja kuvaus kokeiden käytännön järjestelyistä Vaatimusten todentamiseksi tulee toimittaa liittymispisteen verkonhaltijalle viimeistään 2 kk ennen kokeiden aloittamista.
2.2 | Käyttöönoton aikataulu (luku 15.3.1)
Käyttöönoton aikataulu, myöhemmät muutokset käyttöönoton aikatauluun tulee koordinoida liittymispisteen verkonhaltijan ja Fingridin kanssa.
2.3 | Mittausjärjestelyt (luku 15.3.1)
Suunnitelma Vaatimuksiin liittyvien kokeiden mittauksien toteuttamisesta. Tiedot sekä kiinteästi asennettavista että vain käyttöönottokokeiden aikana käytössä olevista mittalaitteista.
3 | Käyttöönottokokeiden tulokset
3.1 | Käyttöönottoraportti Vaatimuksiin liittyvistä kokeista (luku 15.3.3)
3.2 | Käyttöönottokokeiden keskeiset tulokset numeerisessa muodossa (taulukko 16.2)
4 | Todennetut mallinnustiedot
Validoidut dynaamisen toiminnan mallintamiseen tarvittavat tiedot tai laskenmallit (luku 16)
5 | Säätäjien lopulliset asetteluarvot
Sähkövaraston pätötehon ja taajuuden säädön sekä jännitteen ja loistehon säädön lopulliset asetteluarvot.
6 | Suojauksen lopulliset asetteluarvot
Sähkövaraston ja sähkövarastoliitynnän suojauksen lopulliset asetteluarvot.
Vaatimustenmukaisuusilmoitus
Liittyjän edustaja vahvistaa allekirjoituksellaan, että tämän taulukon viitetietojen osoittamat dokumentit todentavat voimalaitoksen täyttävän sille asetetut Vaatimukset. Paikka, aika, allekirjoitus ja nimenselvennys:

## Taulukko 7.3 EN
| Stage 2 (Commissioning and compliance) |  | Ref
1 | Changes and further specifications
Further specifications to the data delivered in stage 1 of the compliance verification process
2 | Data related to commissioning tests
2.1 | Commissioning test plan (section 15.3.1)
The detailed commissioning testing plan, commissioning instructions provided by the grid energy storage system supplier and a description of the practical arrangements of the tests for verifying compliance with the Specifications shall be submitted to the relevant network operator at the latest two months before the tests are started.
2.2 | Commissioning schedule (section 15.3.1)
Commissioning schedule; subsequent changes to the commissioning schedule shall be co-ordinated with the relevant network operator and Fingrid.
2.3 | Measurement arrangements (section 15.3.1)
Plan of the execution of measurements for the tests related to the Specifications. Data on both fixed measuring equipment and measuring equipment only used during the commissioning tests.
3 | Results of commissioning tests
3.1 | Commissioning report on tests related to the Specifications (section 15.3.3)
3.2 | Key results of commissioning tests in numerical format (table 16.2)
4 | Verified modelling data
Validated data required for the modelling of dynamic operation, or simulation models (chapter 16)
5 | Final controller setpoint values
Final setpoint values of the control of active power and frequency as well as of the control of voltage and reactive power of the grid energy storage system.
6 | Final protection setpoint values
Final protection setpoint values of the grid energy storage system and the grid energy storage system connection.
Statement of compliance
The grid energy storage system owner’s representative confirms with a signature that the documents referred to in this table’s reference details prove that the grid energy storage system meets the Specifications set for it. Place, date, signature and printed name: