## VJV2024 Taulukko 7.1
1 | Yleistiedot |  |  | Viite
| 1.1 | Sähköpääkaavio (single line diagram)
| 1.2 | Rakenne
Voimalaitoksen tyyppi (esim. tuulivoima, aurinkovoima, biomassa, kaasutus)
Perustiedot (esim. tuulivoimalaitoksesta tornin korkeus, roottorin halkaisija, suuntaajakäyttö yms.)
| 1.3 | Sijaintitieto (paikkakunta, alue, liittymispiste, koordinaatit)
| 1.4 | Tietoliikenneyhteyksien yhteyskaavio (CSA, Common Service Architecture) ja tietoturvasuunnitelma
2 | Muuntajien tekniset tiedot:
| 2.1 | Voimalaitoksen muuntajien lukumäärä, toimittaja- ja tyyppitiedot
| 2.2 | Muuntajien dokumentaatio ja datalehdet
Teho [MVA], virta [A], muuntosuhde [ensiö/toisio], oikosulkuimpedanssi [%], oikosulkuresistanssi [%], kytkentäryhmä ja maadoitustiedot, käämikytkimen säätöalue ja askel [%,%], käämikytkimen askeleiden määrä ja valittu askel [kpl, askel]
3 | Voimalaitoksen tekniset tiedot:
| 3.1 | Sähköntuotantoyksiköiden lukumäärä, toimittaja- ja tyyppitiedot
| 3.4 | Sähköntuotantoyksiköiden dokumentaatio ja datalehdet
Näennäisteho [MVA], mitoitusteho [MW], maksimiteho [MW], minimiteho[MW], virta [A], jännite [V], taajuus [Hz]
Tahtikoneista sähköiset parametrit (resistanssit, reaktanssit ja niihin liittyvät aikavakiot) ks. taulukko 7.4
| 3.5 | Tuotantotehon riippuvuus käyttöolosuhteista (esim. tuulen voimakkuus, lämpötila)
| 3.6 | Mahdollisesti käytössä olevat kompensointi- ja/tai tehokertoimen korjaamisessa käytettävät laitteet
Lukumäärä, tyyppi, mitoitusarvot (teho, virta, jännite, taajuus)
Mikäli hyödynnetään yliaaltojen suodatukseen, tiedot rakenteesta ja viritystaajuudesta
4 | Voimalaitoksen ominaisuudet:
Seuraavat kohdat voidaan korvata esim. valmistajan laitedokumenteilla, IEC61400-21 standardin mukaisella testausdokumentaatiolla tai muulla testausdokumentaatiolla
| 4.1 | Tiedot voimalaitoksen loistehokapasiteetista ja generaattoreiden PQ-diagrammit
| 4.2 | Tiedot voimalaitoksen kyvystä toimia ali- ja ylijännitteellä
| 4.3 | Tiedot voimalaitoksen kyvystä toimia ali- ja ylitaajuudella
| 4.4 | Tiedot voimalaitoksen kyvystä toimia jännitehäiriöiden yhteydessä
| 4.5 | Tiedot voimalaitoksen vikavirran syötöstä jännitehäiriön aikana
| 4.6 | Tiedot voimalaitoksen pätötehonsäätöominaisuuksista
| 4.7 | Tiedot voimalaitoksen jännitteensäätöominaisuuksista
5 | Voimalaitoksen suojaustiedot:
| 5.1 | Voimalaitoksen relesuojauskaavio
| 5.2 | Voimalaitoksen lopulliset relesuojausasettelut
| 5.3 | Tiedot saarekesuojan toimintaperiaatteesta
6 | Käyttöönottodokumentit:
| 6.1 | Käyttöönottopöytäkirjat
| 6.2 | Jännitteensäädön lopulliset asetteluarvot ja toimintatila
Vaatimustenmukaisuusilmoitus
Liittyjän edustaja vahvistaa allekirjoituksellaan, että tämän taulukon viitetietojen osoittamat dokumentit todentavat voimalaitoksen täyttävän sille asetetut Vaatimukset. Paikka, aika, allekirjoitus ja nimenselvennys:

## VJV2024 Taulukko 7.1 EN
1 | General data |  |  | Ref
| 1.1 | Single line diagram
| 1.2 | Structure
Type of power generating facility (e.g. wind power, solar power, biomass, gasification)
Basic data (e.g. on wind power park module: tower height, rotor diameter, converter powered etc.)
| 1.3 | Location data (municipality, area, connection point, coordinates)
| 1.4 | Diagram of common service architecture (CSA) and information security plan
2 | Technical details of transformers:
| 2.1 | Number, supplier and type details of the power generating facility’s transformers
| 2.2 | Documentation and data sheets of transformers
Power [MVA], current [A], transformation ratio [primary, secondary], short-circuit impedance [%], short-circuit resistance [%], vector group and earthing details, control range and step of on- or off-load tap-changer [%, %], number of steps of on- or off-load tap-changer and selected step [quantity, step]
3 | Technical details of power generating facility:
| 3.1 | Number, supplier and type details of power-generating units
| 3.4 | Documentation and data sheets of power-generating units
Apparent power [MVA], rated capacity [MW], maximum output [MW], minimum output [MW], current [A], voltage [V], frequency [Hz]
Electric parameters of synchronous machines (resistances, reactances, and related time constants) see Table 7.4
| 3.5 | Dependence of production power on operating conditions (e.g. wind velocity, temperature)
| 3.6 | Potentially used compensation devices and/or devices used for the correction of power factor
Number, type, rated values of devices (power, current, voltage, frequency)
If used for the filtering of harmonics, data on the structure and tuning frequency
4 | Power generating facility operational characteristics:
The following items may be replaced, for example, by the manufacturer's device documents, testing documentation according to the IEC 61400-21 standard or other testing documentation
| 4.1 | Data on the power generating facility’s reactive power capacity and PQ diagrams of generators
| 4.2 | Data on the power generating facility’s ability to operate at undervoltage and overvoltage
| 4.3 | Data on the power generating facility’s ability to operate at underfrequency and overfrequency
| 4.4 | Data on the power generating facility’s ability to operate during voltage disturbances
| 4.5 | Data on the power generating facility’s fault current injection during a voltage disturbance
| 4.6 | Data on the power generating facility’s active power control characteristics
| 4.7 | Data on the power generating facility’s voltage control characteristics
5 | Protection details of the power generating facility:
| 5.1 | Relay protection diagram of the power generating facility
| 5.2 | Final relay protection setpoints of the power generating facility
| 5.3 | Data on the operating principle of island protection
6 | Commissioning documents:
| 6.1 | Commissioning records
| 6.2 | Final setpoint values and mode of voltage control
Statement of compliance
The power generating facility owner’s representative confirms with a signature that the documents referred to in this table’s reference details prove that the power generating facility meets the Specifications set for it. Place, date, signature and printed name:

## VJV2024 Taulukko 7.2
| Vaihe 1 (Suunnittelu) |  | Viite
1 | Yleistiedot
1.1 | Hankkeen nimi ja yhteystiedot, liittymispiste, liittymispisteen verkonhaltija ja yhteystiedot
1.2 | Sähköpääkaavio (single line diagram)
Voimalaitoksen keskeisimmät komponentit ja niitä yhdistävä sähköverkko
Pääkaaviossa esitettyjen komponenttien ja johdinten sähköiset parametrit
1.3 | Tyyppitiedot
Voimalaitoksen tuotantotyyppi ja polttoaine (esim. tuulivoima, vesivoima, lauhdevoima [kivihiili])
Perustiedot (esim. tuulivoimalaitoksesta tornin korkeus, roottorin halkaisija, suuntaajakäyttö yms.)
1.4 | Sijaintitieto (paikkakunta, alue, liittymispiste, koordinaatit)
1.5 | Tietoliikenneyhteyksien yhteyskaavio (CSA, Common Service Architecture) ja tietoturvasuunnitelma (luku 10.3.7)
2 | Tekniset tiedot
2.1 | Sähköntuotantoyksiköiden lukumäärä, toimittaja- ja tyyppitiedot
2.2 | Sähköntuotantoyksiköiden dokumentaatio ja datalehdet
Tuotantoyksiköiden näennäisteho [MVA], mitoitusteho [MW], minimiteho[MW], virta [A], jännite [V], taajuus [Hz]
Tahtikoneista taulukon 7.4 mukaiset tiedot
Vesivoimalaitoksista vesiaikavakio (Tw)
2.3 | Muuntajien dokumentaatio ja datalehdet
Teho [MVA], virta [A], muuntosuhde [ensiö/toisio], oikosulkuimpedanssi [%], oikosulkuresistanssi [%], kytkentäryhmä ja maadoitustiedot, käämikytkimen säätöalue ja askel [%,%], käämikytkimen askeleiden määrä ja valittu askel [kpl, askel]
2.4 | Muiden komponenttien dokumentaatio ja datalehdet
Soveltuvin osin vastaavat tiedot kuin sähköntuotantoyksiköistä (kohta 2.2) ja muuntajista (kohta 2.3) sekä kaikki ne tiedot, joilla on merkitystä Vaatimusten kannalta (esim. rakenne, suodattimen viritystaajuus)
3 | Jännite-taajuus toiminta-alue
3.1 | Tiedot voimalaitoksen kyvystä toimia ali- ja ylijännitteellä (luku 10.2.1 tai 10.5.2)
3.2 | Tiedot voimalaitoksen kyvystä toimia ali- ja ylitaajuudella (luku 10.2.1 tai 10.5.2)
3.3 | Tiedot voimalaitoksen taajuuden muutosnopeuden sietokyvystä (luku 10.2.2)
4 | Lähivika- ja ylijännitekestoisuus
4.1 | Laskelma voimalaitoksen toiminnasta jännitehäiriön aikana ja mahdolliset tehdaskokeiden raportit (luku 10.3.2 tai 10.5.3)
4.2 | Tiedot voimalaitoksen toiminnasta lyhytaikaisen ylijännitteen aikana (luku 10.3.3)
4.3 | Tiedot suuntaajakytketyn voimalaitoksen loisvirran syötöstä (luku 18.1.2)
4.4 | Tiedot pätötehon palautumisesta jännitehäiriön jälkeen (luku 10.3.4)
5 | Pätötehon ja taajuuden säätö
5.1 | Dokumentaatio ja kuvaus pätötehon ja taajuuden säädöstä (luku 11 tai 16)
Dokumentaatio säätöjärjestelmän toteutuksesta ja teknisista ominaisuuksista.
Siirtofunktioina kuvattu toiminnallinen lohkokaavioesitys säädön toteutuksesta (vain tahtikonevoimalaitokset, esim. IEEE PES-TR1 mukaan).
5.2 | Säätäjille aseteltavat parametrit ja toimintaviiveet
6 | Omakäyttö ja tuotantotehon muutokset
6.1 | Tiedot voimalaitoksen toiminnasta omakäytöllä (luku 11.3.5)
Voimalaitoksen omakäyttötehon suuruus, toiminta-aika omakäytöllä, mahdolliset viiveet omakäytölle siirtymisen ja verkkoon tahdistumisen suhteen sekä omakäytölle siirtymisen rajoitteet
6.2 | Tuotantotehon muutokset
Tuotantotehon muutokset taajuus- ja jännitevaihteluiden yhteydessä
Tuotantotehon riippuvuus käyttöolosuhteista (esim. lämpötila, tuulen nopeus)
Tuotantotehon alasajoon johtavat käyttöolosuhteet (esim. maksituulennopeuden raja-arvo)
Tuotantotehon muutosnopeus, muutosnopeuden rajoittimien toiminnallisuus sekä rajoitteet
7 | Voimalaitoksen loistehokapasiteetti
7.1 | Loistehokapasiteettilaskelma (luku 12.2.4 tai 17.2.4)
7.2 | PQ-diagammit
Voimantuotantoyksiköiden tai generaattoreiden PQ-diagammit sekä tiedot niiden jännite-taajuusriippuvuudesta. PQ-diagrammeihin tulee merkitä loistehoa rajoittavien rajoittimien asettelut.
7.3 | Muut loistehoon vaikuttavat komponentit
Loistehoa tuottavat (esim. kondensaattori tai STATCOM) ja kuluttavat komponentit sekä niiden toiminta komponentteihin vaikuttavien suureiden (esim. jännite, pätöteho) funktiona
8 | Jännitteen ja loistehon säätö
8.1 | Dokumentaatio ja kuvaus jännitteen ja loistehon säädöstä (luku 13 tai 18)
Dokumentaatio säätöjärjestelmän toteutuksesta ja teknisista ominaisuuksista.
Siirtofunktioina kuvattu toiminnallinen lohkokaavioesitys säädön toteutuksesta (tahtikonevoimalaitoksille esim. IEEE 421.5 mukaan, suuntaajakytketyillä periaatetason lohkokaavioesitys).
8.2 | Säätäjille aseteltavat parametrit ja toimintaviiveet
8.3 | Jännitteensäädön suorituskykylaskelma (luku 13.2.3 tai 18.2.2.1)
9 | Voimalaitoksen suojausasettelut ja vaikutus sähkön laatuun
9.1 | Suojausasettelut (luku 10.3.5)
Tiedot generaattoreiden ja laitostason relesuojauskaaviosta ja kuvattujen suojien asetteluista. Tiedot on toimitetettava suojista, jotka johtavat generaattorin/laitoksen verkosta irtoamiseen sekä suojista, joiden toiminta johtaa generaattorin/voimalaitoksen pätötehon, loistehon tai jännitteen rajoittamiseen tai automaattiseen muuttamiseen.
9.2 | Voimalaitoksen vaikutus sähkön laatuun (luku 10.4.5)
Kuvaus voimalaitoksen verkkoonliittymisen aiheuttamasta sähkön laadun muutoksesta sekä mahdolliset tehdaskokeiden raportit (esim. IEC61400-21) mukaan.
10 | Dynaamisen toiminnan laskentaan tarvittavat tiedot
Projektikohtaiset dynaamisen toiminnan mallintamiseen tarvittavat tiedot tai laskentamallit Vaatimusten mukaisesti (luku 15 tai 20)
11 | Reaaliaikaiset mittaustiedot ja instrumentointi
11.1 | Reaaliaikaisten mittaustietojen toimitustapa ja todennus (luku 9.3 ja 10.4.1)
11.2 | Tallentimien tekniset tiedot ja asettelut (luku 9.4 tai 9.5)
12 | Erityistarkasteluvaatimukset
Vaadittavat erityistarkastelut Vaatimuksiin liittyen (luku 5)
13 | Voimalaitosprojektin aikataulu ja käyttöönotto
Voimalaitoshankkeen aikataulu ja Vaatimuksiin liittyvien käyttöönottokokeiden suunniteltu ajankohta. Myös mahdolliset optiot projektin laajentumiselle ja jo tiedossa olevat tulevaisuuden laajennussuunnitelmat tulee ilmoittaa.
Vaatimustenmukaisuusilmoitus
Liittyjän edustaja vahvistaa allekirjoituksellaan, että tämän taulukon viitetietojen osoittamat dokumentit todentavat voimalaitoksen täyttävän sille asetetut Vaatimukset. Paikka, aika, allekirjoitus ja nimenselvennys:

## VJV2024 Taulukko 7.2 EN
| Stage 1 (Planning) |  | Ref
1 | General data
1.1 | Name and contact details of project, connection point, relevant network operator and contact details
1.2 | Single line diagram
The main components of the power generating facility and the electricity network that connects the components
Electric parameters of the components and conductors presented in the single line diagram
1.3 | Type data
Power generating facility’s production type and fuel (e.g. wind power, hydropower, condensing power [coal])
Basic data (e.g. on wind power park module: tower height, rotor diameter, converter powered etc.)
1.4 | Location data (municipality, area, connection point, coordinates)
1.5 | Diagram of common service architecture (CSA) and information security plan
2 | Technical data
2.1 | Number, supplier and type details of power-generating units
2.2 | Documentation and data sheets of power-generating units
Production units’ apparent power [MVA], rated capacity [MW], minimum output [MW], current [A], voltage [V], frequency [Hz]
Data specified in Table 7.4 on synchronous power generating modules
Water time constant of hydroelectric power plants (Tw)
2.3 | Documentation and data sheets of transformers
Power [MVA], current [A], transformation ratio [primary, secondary], short-circuit impedance [%], short-circuit resistance [%], vector group and earthing details, control range and step of on- or off-load tap-changer [%, %], number of steps of on- or off-load tap-changer and selected step [quantity, step]
2.4 | Documentation and data sheets of other components
Where applicable, the same data as on power generating units (section 2.2) and transformers (section 2.3) as well as all data that is relevant in terms of the Specifications (e.g. structure, filter tuning frequency)
3 | Operating voltage and frequency range
3.1 | Data on the power generating facility’s ability to operate at undervoltage and overvoltage (section 10.2.1 or 10.5.1)
3.2 | Data on the power generating facility’s ability to operate at underfrequency and overfrequency (section 10.2.1 or 10.5.1)
3.3 | Data on the power generating facility’s rate of change of frequency withstand capability (section 10.2.2)
4 | Fault-ride-through capability
4.1 | Calculation of the operation of the power generating facility during voltage disturbance, and potential reports on factory testing (section 10.3.2 or 10.5.3)
4.2 | Data on capability to operate during short-time overvoltage (luku 10.3.3)
4.3 | Data on fault current injection of a power park module (section 18.1.2)
4.4 | Data on active power recovery after a voltage disturbance (section 10.3.4)
5 | Active power control and frequency control
5.1 | Documentation and description of active power control and frequency control (chapter 11 or 16)
Documentation on the control system’s implementation and technical characteristics.
Functional block diagram on the implementation of control described as transfer curves. (E.g. according to IEEE PES-TR1).
5.2 | Parameters and operating delays set for controllers
6 | House load and changes in production power
6.1 | Data on the operation of the power generating facility in house load operation (section 11.3.5)
Magnitude of house load of the power generating facility, operating time in house load operation, potential delays in terms of transition to house load operation and synchronisation with the grid, and restrictions in terms of transition to house load operation
6.2 | Changes in production power
Changes in production power in conjunction with frequency and voltage fluctuations
Dependence of production power on operating conditions (e.g. temperature, wind velocity)
Operating conditions leading to the shutdown of production power (e.g. limit value of maximum wind velocity)
Rate of change of production power, functionality and constraints of limiters of rate of change
7 | Reactive power capacity of the power generating facility
7.1 | Reactive power capacity calculation (section 12.2.4 or 17.2.4)
7.2 | PQ diagrams
PQ diagrams of power generating units or generators and data on their voltage-frequency dependence. The setpoints used in the reactive power limiters shall be specified in the PQ diagrams.
7.3 | Other components influencing reactive power
Components that generate (e.g. capacitor or STATCOM) and consume reactive power, and their operation as a function of the variables (e.g. voltage, active power) influencing the components
8 | Voltage control and reactive power control
8.1 | Documentation and description of voltage control and reactive power control (chapter 13 or 18)
Documentation on the control system’s implementation and technical characteristics.
Functional block diagram on the implementation of control described as transfer curves. (e.g. according to IEEE 421.5).
8.2 | Parameters and operating delays set for controllers
8.3 | Voltage control performance calculation (section 13.2.3 or 18.2.2.1)
9 | Protection setpoints of the power generating facility and impact on power quality
9.1 | Protection setpoints (section 10.3.5)
Data on the relay protection diagram of the generators and at the facility level as well as on the setpoints of the described protection. Related data shall be submitted on protection which leads to the disconnection of the generator/facility from the grid and on protection whose activation leads to a restriction or automatic change in the generator’s/power generating facility’s active power, reactive power or voltage.
9.2 | The power generating facility’s impact on power quality (section 10.4.4).
Description of the change in power quality caused by the connection of the power generating facility to the grid, and potential reports of factory testing (e.g. according to IEC 61400-21).
10 | Data required for dynamic modelling
Project-specific data or simulation models required by the modelling of dynamic operation in accordance with the Specifications (Chapter 15 or 20)
11 | Real-time measurement data and instrumentation
11.1 | Method of delivery and verification of real-time measurement data (section 9.3)
11.2 | Technical data on and the setpoints of disturbance and swing recorders
12 | Specific study requirements
Required specific studies related to the Specifications (chapter 5)
13 | Power generating facility project’s schedule and commissioning
Schedule of the power generating facility project and the planned timing of the commissioning tests relating to the Specifications. Possible options for expanding the project and known future expansion plans shall also be reported.
Statement of compliance
The power generating facility owner’s representative confirms with a signature that the documents referred to in this table’s reference details prove that the power generating facility meets the Specifications set for it. Place, date, signature and printed name:

## Taulukko 7.3
| Vaihe 2 (Käyttöönotto ja todentaminen) |  | Viite
1 | Muutokset ja täsmennykset
Muutokset ja täsmennykset todentamisprosessin vaiheessa 1 toimitettuihin tietoihin
2 | Käyttöönottokokeisiin liittyvät tiedot
2.1 | Käyttöönottokoesuunnitelma (luku 14.3.1 tai 19.3.1)
Yksityiskohtainen käyttöönottokoesuunnitelma, voimalaitostoimittajan antamat käyttöönotto-ohjeet ja kuvaus kokeiden käytännön järjestelyistä Vaatimusten todentamiseksi tulee toimittaa liittymispisteen verkonhaltijalle viimeistään 2 kk ennen kokeiden aloittamista.
2.2 | Käyttöönoton aikataulu (luku 14.3.1 tai 19.3.1)
Käyttöönoton aikataulu, myöhemmät muutokset käyttöönoton aikatauluun tulee koordinoida liittymispisteen verkonhaltijan ja Fingridin kanssa.
2.3 | Mittausjärjestelyt (luku 14.3.1 tai 19.3.1)
Suunnitelma Vaatimuksiin liittyvien kokeiden mittauksien toteuttamisesta. Tiedot sekä kiinteästi asennettavista että vain käyttöönottokokeiden aikana käytössä olevista mittalaitteista.
3 | Käyttöönottokokeiden tulokset
3.1 | Käyttöönottoraportti Vaatimuksiin liittyvistä kokeista (luku 14.3.3 tai 19.3.3)
3.2 | Käyttöönottokokeiden keskeiset tulokset numeerisessa muodossa (taulukko 15.2 tai 20.2)
4 | Todennetut mallinnustiedot
Validoidut dynaamisen toiminnan mallintamiseen tarvittavat tiedot tai laskenmallit (luku 15 tai 20)
5 | Säätäjien lopulliset asetteluarvot
Voimalaitoksen/generaattoreiden pätötehon ja taajuuden säätäjien sekä jännitteen ja loistehon säätäjien lopulliset asetteluarvot.
6 | Suojauksen lopulliset asetteluarvot
Voimalaitoksen/generaattoreiden ja voimalaitosliitynnän suojauksen lopulliset asetteluarvot.
Vaatimustenmukaisuusilmoitus
Liittyjän edustaja vahvistaa allekirjoituksellaan, että tämän taulukon viitetietojen osoittamat dokumentit todentavat voimalaitoksen täyttävän sille asetetut Vaatimukset. Paikka, aika, allekirjoitus ja nimenselvennys:

## Taulukko 7.3 EN
| Stage 2 (Commissioning and compliance) |  | Reference
1 | Changes and further specifications
Further specifications to the data delivered in stage 1 of the compliance verification process
2 | Data related to commissioning tests
2.1 | Commissioning test plan (section 14.3.1 or 19.3.1)
The detailed commissioning testing plan, commissioning instructions provided by the power generating facility supplier and a description of the practical arrangements of the tests for verifying compliance with the Specifications shall be submitted to the relevant network operator at the latest two months before the tests are started.
2.2 | Commissioning schedule (section 14.3.1 or 19.3.1)
Commissioning schedule; subsequent changes to the commissioning schedule shall be co-ordinated with the relevant network operator and Fingrid.
2.3 | Measurement arrangements (section 14.3.1 or 19.3.1)
Plan of the execution of measurements for the tests related to the Specifications. Data on both fixed measuring equipment and measuring equipment only used during the commissioning tests.
3 | Results of commissioning tests
3.1 | Commissioning report on tests related to the Specifications (section 14.3.3 or 19.3.3)
3.2 | Key results of commissioning tests in numerical format (Table 15.2 or 20.2)
4 | Verified modelling data
Validated data required for the modelling of dynamic operation, or simulation models (chapter 15 or 20)
5 | Final controller setpoint values
Final setpoint values of the controllers of active power and frequency as well as of the controllers of voltage and reactive power of the power generating facility/generators.
6 | Final protection setpoint values
Final protection setpoint values of the power generating facility/generators and the power generating facility connection.
Statement of compliance
The power generating facility owner’s representative confirms with a signature that the documents referred to in this table’s reference details prove that the power generating facility meets the Specifications set for it. Place, date, signature and printed name:

## Taulukko 7.4
1 | Mitoitusarvot
1.1 | Mitoitusjännite Ur | [kV]
1.2 | Jännitealue | [p.u.]
1.3 | Näennäisteho Sr | [MVA]
1.4 | Mitoitusteho Pmax | [MW]
1.5 | Mitoitusvirta Ir | [A]
1.6 | Mitoitustehokerroin cos ϕr
1.7 | Mitoituspyörimisnopeus n | [1/min]
1.8 | Mitoitusmagnetointijännite Ue | [V]
1.9 | Mitoitusmagnetointivirta If | [A]
2 | Impedanssit
2.1 | Staattoriresistanssi R | [p.u.]
2.2 | Pitkittäinen tahtireaktanssi Xd | [p.u.]
2.3 | Pitkittäinen tahtireaktanssi Xd (kyllästynyt) | [p.u.]
2.4 | Poikittainen tahtireaktanssi Xq | [p.u.]
2.5 | Pitkittäinen muutosreaktanssi Xd' | [p.u.]
2.6 | Pitkittäinen muutosreaktanssi Xd' (kyllästynyt) | [p.u.]
2.7 | Poikittainen muutosreaktanssi Xq' | [p.u.]
2.8 | Pitkittäinen alkureaktanssi Xd" | [p.u.]
2.9 | Poikittainen alkureaktanssi Xq" | [p.u.]
2.10 | Staattorin hajareaktanssi Xl | [p.u.]
2.11 | Nollareaktanssi X0 | [p.u.]
2.12 | Vastareaktanssi X2 | [p.u.]
3 | Aikavakiot
3.1 | Tasakomponentin aikavakio Ta | [s]
3.2 | Pitkittäinen tyhjäkäyntimuutosaikavakio Tdo' | [s]
3.3 | Poikittainen tyhjäkäyntimuutosaikavakio Tqo' | [s]
3.4 | Pitkittäinen tyhjäkäyntialkuaikavakio Tdo" | [s]
3.5 | Poikittainen tyhjäkäyntialkuaikavakio Tqo" | [s]
3.6 | Pitkittäinen muutosaikavakio Td' | [s]
3.7 | Poikittainen muutosaikavakio Tq' | [s]
3.8 | Pitkittäinen alkuaikavakio Td" | [s]
3.9 | Poikittainen alkuaikavakio Tq" | [s]
4 | Mekaaniset parametrit
4.1 | Hitausvakio (turpiini, generaattori ja muut pyörivät komponentit) H | [s]
4.2 | Generaattorin hitausmomentti Jg | [kgm²]
4.3 | Kunkin turpiinin hitausmomentti Jt1, Jt2, Jt3, .... | [kgm²]
4.4 | Magnetointikoneen (jos käytössä) hitausmomentti Jexc | [kgm²]
4.5 | Edellä annettujen turpiinigeneraattorien osien väliset jousivakiot Kt1_t2 , Kt2_t3 , ..., Ktx_g , Kg_exc | [Nm/Rad]

## Taulukko 7.4 EN
1 | Rated values
1.1 | Rated voltage Ur | [kV]
1.2 | Voltage range | [pu]
1.3 | Apparent power Sr | [MVA]
1.4 | Rated capacity Pmax | [MW]
1.5 | Rated current Ir | [A]
1.6 | Rated power factor cos ϕr
1.7 | Rated speed of rotation n | [1/min]
1.8 | Rated excitation voltage Ue | [V]
1.9 | Rated excitation current If | [A]
2 | Impedances
2.1 | Stator resistance R | [pu]
2.2 | Direct-axis synchronous reactance Xd | [pu]
2.3 | Direct-axis synchronous reactance Xd (saturated) | [pu]
2.4 | Quadrature-axis synchronous reactance Xq | [pu]
2.5 | Direct-axis transient reactance Xd' | [pu]
2.6 | Direct-axis transient reactance Xd' (saturated) | [pu]
2.7 | Quadrature-axis transient reactance Xq' | [pu]
2.8 | Direct-axis subtransient reactance Xd" | [pu]
2.9 | Quadrature-axis subtransient reactance Xq" | [pu]
2.1 | Stator stray reactance Xl | [pu]
2.11 | Zero phase-sequence reactance X0 | [pu]
2.12 | Negative phase-sequence reactance X2 | [pu]
3 | Time constants
3.1 | DC short-circuit time constant Ta | [s]
3.2 | Direct-axis transient open circuit time constant Tdo' | [s]
3.3 | Quadrature-axis transient open circuit time constant Tqo' | [s]
3.4 | Direct-axis subtransient open circuit time constant Tdo" | [s]
3.5 | Quadrature-axis subtransient open circuit time constant Tqo" | [s]
3.6 | Direct-axis transient short-circuit time constant Td' | [s]
3.7 | Quadrature-axis transient short-circuit time constant Tq' | [s]
3.8 | Direct-axis subtransient short-circuit time constant Td" | [s]
3.9 | Quadrature-axis subtransient short-circuit time constant Tq" | [s]
4 | Mechanical parameters
4.1 | Inertia constant (turbine, generator and other rotating components) H | [s]
4.2 | Moment of inertia of generator Jg | [kgm²]
4.3 | Moment of inertia of each turbine Jt1, Jt2, Jt3, .... | [kgm²]
4.4 | Moment of inertia of exciter (if available) Jexc | [kgm²]
4.5 | Spring constants between the above-mentioned turbine generator parts Kt1_t2 , Kt2_t3 , ..., Ktx_g , Kg_exc | [Nm/Rad]