## Introduction
NOTE: Read Grid Code chapters 6.4.3.2 in VJV2024 and SJV2024
Main Purpose of this excel is review the initial technical data for the project and its key design principles. In this excel the technical topics are highlighted which at least must be considered in early design phase of the power plant or energy storage system or hybrid power plant, even before placing the Purchase Orders. Topics listed in this excel are based on the experience from the past projects. Also New requirements (2024), which are greatly affecting to the design are introduced.
Step by step instructions for the Connectee for Stage 0 meeting for type D | Step by step instructions for type B
1. Request project specific grid data from Fingrid (SCR, VCSCR, ESCR -values) Contact info: vikavirrat@fingrid.fi. Please include: 1.1 … 1.12 of Stage 0 Questionnaire in request. | Tool is added to help RSO/DSO and Connectee communication during initial phase of connection. DSO/RSO sets the process. Fingrid is not involved in this process if asset is not connected to Fingrid. Excel can be uploaded to Oma Fingrid but upload is not required by Fingrid. Main Purpose of this excel is review the initial technical data for the project and its key design principles. In this excel the technical topics are highlighted which at least must be considered in early design phase of the power plant or energy storage system or hybrid power plant, even before placing the Purchase Orders. Topics listed in this excel are based on the experience from the past projects.
2. Request Specific Study requirements from Fingrid (Grid Code Chapter 5) Contact info: gridcompliance@fingrid.fi. Please include: 1.1 … 1.12 of Stage 0 Questionnaire in request.
3. Go through sheet "Stage 0 Questionnaire" with relevant engineers and relevant parties in your Project
4. Fill the data and the feedback from OEM(s) you have for the chapters
5. Arrange meeting with Fingrid and relevant network operator (if there is DSO/RSO), Excel is updated and kept as meeting log
6. Agree the next steps

## Stage 0 Questionnaire Type D
Stage 0 Pre-design phase
1 | General data
1.1 | Name of the project (used in connection enquiry)
1.2 | Company name in grid connection agreement
| 1.2.1 | Business ID
| 1.2.2 | Business name
| 1.2.3 | Contact information (email + name + phone number)
1.3 | Project developer
| 1.3.1 | Business ID
| 1.3.2 | Business name
| 1.3.3 | Contact information (email + name + phone number)
1.4 | Property identifiers (FI: Kiinteistötunnukset) of asset build location
| 1.4.1 | Substation
| 1.4.2 | Power generating or energy storage facilities
| 1.4.3 | Crossing statement Ids (FI: Risteämälausunto tunnukset), if applicable. More info from https://www.fingrid.fi/en/grid/land-use-and-environment/license-and-statement/
1.5 | Description of project and project relation to any other projects
1.6 | My Fingrid customer portal (FI: Oma Fingrid) project links (leave empty if not known during intial query)
| 1.6.1 | Power plant project
| 1.6.2 | Connection project
1.7 | Type of the power plant (Wind, Solar, BESS etc.)
1.8 | Connection point
| 1.8.1 | Connection point to Fingrid grid
| 1.8.2 | Connection point to DSO/RNO network (if applicable)
| 1.8.3 | Voltage level of connection point
| 1.8.4 | Connection method and description
| 1.8.5 | Length of cable/powerline to asset substation
| 1.8.6 | Electrical description of used cable/powerline (type, conductor etc. )
1.9 | Grid Owner of the connection point
1.10 | Estimated date to start the production? (Target date for ION )
1.11 | Rated power of the power plant [MW] (active power at HV-side of main transformer(s))
| 1.11.1 | Minimum planned Rated capacity in production mode (Pmax,p)
| 1.11.2 | Maximum planned Rated capacity in production mode (Pmax,p)
| 1.11.3 | Minimum planned Rated capacity in demand mode (Pmax,d)
| 1.11.4 | Maximum planned Rated capacity in demand mode (Pmax,d)
| 1.11.5 | Information about different assets and their rated power (BESS, WIND , SOLAR … ) ONLY FILL IN HYBRID PROJECTS
1.12 | Installed capacity [MW] (e.g. how many turbines/inverters and what rating)
1.13 | Has fault current levels and voltage control tuning data (VCSCR) been requested already from vikavirrat@fingrid.fi?
1.14 | Has evaluation of Specific Study requirements (chapter 5) already been requested from Fingrid? Contact info: gridcompliance@fingrid.fi, include at least section 1.1 … 1.12 of this documents
| 1.14.1 | Date of specific study requirements (letter) received
| 1.14.2 | Date of expiration of specific study requirements (letter) received
1.15 | Has the Grid Code Consultant already been chosen? Who will run the simulation studies?
1.16 | Is this the first time that the supplier of turbines or inverters delivers the project in Finland?
1.17 | Has the Relevant Operator (RO) been chosen?
1.18 | Is it scheduled that the planning data is delivered to Fingrid six months before start of the production? (Before ION)
| 1.18.1 | Aware of new PSS/E v36 version requirement and latest modelling instructions?
| 1.18.2 | Aware of PSCAD modelling instructions Appendix A unit model validation requirements?
| 1.18.3 | Aware of model validation test templates and tests shall be passed before submission of models?
1.19 | Persons participating in Stage 0 meeting (This is filled in during Stage 0 meeting)
| 1.19.1 | Fingrid
| 1.19.2 | RSO/DSO
| 1.19.3 | Connectee
| 1.19.4 | Date and Time of the meeting
| Specific study requirements (ONLY FILL REQUIREMENTS THAT ARE GIVEN IN SPECIFIC STUDY REQUIREMENT LETTER) |  |  |  | Referred chapter
2 |  |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
2.1 | Operation in IBR dominated Grid
| 2.1.1 | Low ESCR and VCSCR values - can the plant operate in stable manner? (Converter OEM should verify this)
| 2.1.2 | Specific pre-studies to be done to show this before choosing the supplier? (Stage-0 screening)
2.2 | Is the plant located in SSO area?
| 2.2.1 | SSO damping - DFIG OEM has SSO damping function? How to benchmark it, i.e. how to evaluate performance?
| 2.2.2 | SSO protection - to be implemented at unit level (at turbines) or at substation level?
2.3 | Is POD required by Fingrid? - (this is rarely needed)
2.4 | Specific protection or control arrangements? Temporary connections?
2.5 | Geomagnetically induced currents (GIC)? - especially on 400 kV connectees
2.6 | Power Quality ? - If required - monitoring devices and instrument transformers
Top-level Control Philosophy
3 |  |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
3.1 | Reference point for Voltage Control (POM)
3.2 | Reference point(s) for Active power Control (POM(s))
3.3 | Reactive power limits at the point of connection (reactive power window)? How this is taken into account in control design?
| 3.3.1 | LDC or Vref set-point optimization?
| 3.3.2 | If Line Droop Compensation (LDC) is used, is this the first time OEM is about to implement this in Finland?
| 3.3.3 | Compensation of the connecting line needed during no production (night for solar power, not windy for wind power)?
3.4 | How many Power Park Controllers (PPC) will there be at site?
3.5 | Is the PPC supplier same as the converter supplier?
3.6 | Is there redundancy or fall-backs regarding to Power Park Controllers (PPC) if e.g. Master controller fails?
3.7 | What happens for the Power Park Controller (PPC) in event of measurement failure? |  |  |  | Chapter 18 | Chapter 13
| 3.7.1 | This will be tested in test 11) in VJV2024 and test 10) in SJV2024 |  | include these in the specifications! | Chapter 19 | Chapter 15
Balance of Plant
4 |  |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
4.1 | Is there a need for point-on-wave switching i.e. single pole operated breakers according to YLE2021/DSO requirements?
4.2 | Main transformers
| 4.2.1 | What is the Un at HV-side? (note 110 kV system operation voltage is 118 kV and 400 kV system is 410 kV) |  |  | Chapter 10
| 4.2.2 | Start point arrangements; Reactor needed ? Resistors needed for GIC by Fingrid? (especially 400 kV connectees)
| 4.2.3 | Is there On-load tap changer (OLTC)? If no, has this been considered in reactive power capacity calculations?
| 4.2.4 | Connection to overhead line?
If yes, is the transformer zk high enough for Fingrid's protection selectivity requirement? (YLE2021)
4.3 | Disturbance and Swing recorders chosen and location clear? |  |  |  | Chapter 9
| 4.3.1 | Continuously measuring device? |  |  | Chapter 9
| 4.3.2 | Can they meet the measurement accuracy and data storage as required? |  |  | Chapter 9
| 4.3.3 | How to ensure that Fingrid will receive records within 8 hours after requests? |  |  | Chapter 9
4.4 | Protection design shall consider that the plant will not trip during LVRT/HVRT, voltage and frequency dips or other grid events
| 4.4.1 | Note new high voltage ride through requirement
| 4.4.2 | If overhead line connection to Fingrid - has "Local disconnection relay" included?
4.5 | Voltage and active power control implemented at site CT's and VT's (no measurements from FG's substation is allowed!)
General Performance requirements
5 |  |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
5.1 | Reactive power requirement - is the point of requirement clear (HV side of main transformer) ? |  |  |  | Chapter 17
|  | Is there need for capacitor banks? If yes - does it have detuning reactors? Does it have specific breaker? Overvoltage protections? |  |  | Chapter 17
5.2 | Is the supplier aware of the active power prioritization requirement, if the LVRT mode is not activated? |  |  |  | Chapter 10 and 18
5.3 | Is this the first time the inverter supplier and power park controller supplier deliver a project together?
| 5.6.1 | If yes, are you aware of communication risks regarding to delays and grid compliance? How to mitigate the risk (FAT's?)?
| 5.6.2 | If no, how to ensure that voltage control response requirement is met regarding to communication/protocol delays?
Performance requirements for Wind and Solar (ONLY VALID FOR WIND AND SOLAR PROJECTS)
6 |  |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
6.1 | Is the supplier aware of new requirement of voltage control tuning? (fast rise time min 5 % / 30 ms)? |  |  |  | Chapter 18
|  | Has the supplier confirmed e.g. by simulation models and FAT tests that they have the technology for the requirement? |  |  | Chapter 18
6.2 | Is the supplier aware of the new fault current infeed requirements? |  |  |  | Chapter 18
6.3 | Has the new HVRT requirement noted in the design? Is the turbine/converter OEM aware of this? |  |  |  | Chapter 10
Performance requirements for BESS (ONLY VALID FOR ENERGY STORAGE PROJECTS)
7 |  |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
7.1 | Has the supplier been informed about the Grid Forming (GFM) requirements? |  |  |  |  | Chapter 10
7.2 | Is this the first time the inverter supplier delivers Grid Tied Grid Forming inverter?
| 7.2.1 | If yes, how to mitigate risk of not fulfilling Fingrid's requirements regarding to GFM?
7.3 | Is this the first time the inverter supplier and power park controller supplier deliver a project together?
| 7.3.1 | If yes, are you aware of communication risks regarding to delays and grid compliance? How to mitigate the risk?
| 7.3.2 | If no, can they meet the requirements of Fingrid regarding to communication/protocol delays?
7.4 | Has the new HVRT requirement noted in the design? Is the converter OEM aware of this? |  |  |  |  | Chapter 10
7.5 | How to ensure safe disconnection from the grid if there will be Islanding? (GFM BESS cannot rely on local EVY)
8 | Remote Controllability and Power Park controller |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
8.1 | Is the power park controller supplier aware of new signals required to be exchanged / controlled by the operator? |  |  |  | Chapter 10 | Chapter 10
8.2 | Is the Relevant Operator (RO) aware of new signals required to be changed/ controlled? |  |  |  | Chapter 10 | Chapter 10
8.3 | Is control prioritization between RO,OEM, Aggregator etc. clear how to implement it in the PPC ? |  |  |  | Chapter 10 | Chapter 10
| 8.3.1 | This is tested in test 12) VJV2024 and test 11) SJV2024 |  |  | Chapter 19 | Chapter 15
8.4 | Autonomous connection after losing external network connections has this been designed? |  |  |  | Chapter 10 | Chapter 10
| 8.4.1 | This is tested in test 13) VJV2024 and test 12) SJV2024 |  |  | Chapter 19 | Chapter 15
9 | Telecommunications and information security |  |  |  | VJV2024 | SJV2024 | Project (BOP design) | OEM 1 | OEM 2 | OEM 3 | OEM 4
9.1 | Telecommunications and information security - has this been considered? |  |  |  | Chapter 10 | Chapter 10
| 9.1.1 | See Cybersecurity survey from https://www.fingrid.fi/kantaverkko/liitynta-kantaverkkoon/tekniset-vaatimukset/jarjestelmateknisia-vaatimuksia-taydentavat-dokumentit/ |  |  | Chapter 10 | Chapter 10
9.2 | Have you considered any redundancy for the connections?
9.3 | Has NCER requirements considered in the project already?
9.4 | Has project familiar with Requirements for the Reliability of Reserve Provision? |  |  |  | Not SJV/VJV related)
| 9.4.1 | See material from Fingrid reserve market details https://www.fingrid.fi/sahkomarkkinat/reservit/reservituotteet-ja-markkinoille-osallistuminen/ |  |  | Not SJV/VJV related)

## Questionnaire for Type B
Pre-design phase
1 | General data
1.1 | Name of the project (used in connection enquiry)
1.2 | Company name in grid connection agreement
| 1.2.1 | Business ID (FI: Y-tunnus)
| 1.2.2 | Business name
| 1.2.3 | Contact information (email + name + phone number)
1.3 | Project developer
| 1.3.1 | Business ID (FI: Y-tunnus)
| 1.3.2 | Business name
| 1.3.3 | Contact information (email + name + phone number)
1.4 | Property identifiers (FI: Kiinteistötunnukset) of asset build location
| 1.4.1 | Substation
| 1.4.2 | Power generator assets
| 1.4.3 | Crossing statement Ids (FI: Risteämälausunto tunnukset), if applicable.
1.5 | Description of project and project relation to any other projects
1.6 | My Fingrid customer platform (FI: Oma Fingrid) project links (https://oma.fingrid.fi/fi )
| 1.6.1 | Power plant project
| 1.6.2 | Who will deliver data to My Fingrid (Oma Fingrid), DSO/RNO or Connectee?
1.7 | Type of the power plant (Wind, Solar, BESS etc.)
1.8 | Connection point
| 1.8.1 | Connection point to Fingrid grid
| 1.8.2 | Connection point to DSO/RSO network
| 1.8.3 | Voltage level of connection point
| 1.8.4 | Connection method and description
| 1.8.5 | Length of cable/powerline to asset substation
| 1.8.6 | Electrical description of used cable/powerline (type, conductor etc. )
1.9 | Grid Owner and RSO of the connection point
1.10 | Estimated date to start the production? (Target date for ION )
1.11 | Rated power of the power plant [MW] (active power at HV-side of main transformer(s))
| 1.11.1 | Minimum planned Rated capacity in production mode (Pmax,p)
| 1.11.2 | Maximum planned Rated capacity in production mode (Pmax,p)
| 1.11.3 | Minimum planned Rated capacity in demand mode (Pmax,d)
| 1.11.4 | Maximum planned Rated capacity in demand mode (Pmax,d)
| 1.11.5 | Information about different assets and their nominal power (BESS, WIND , SOLAR … )
1.12 | Installed capacity [MW] (e.g. how many turbines and what rating)
1.13 | Is this the first time that the supplier of turbines or inverters delivers the project in Finland?
1.14 | Has the Relevant Operator (RO) been chosen?
1.15 | Links to DSO/RSO connection terms and technical manuals implemented this project
1.16 | Grid connection agreement
| 1.16.1 | Status of Connection agreement enquiry to Fingrid
| 1.16.2 | Date of Grid connection agreement (if already done)
| 1.16.3 | Grid connection agreement capacity
| 1.16.4 | Is connection agreement in MVA or in MW? How this limit is implemented on site?
1.17 | Short circuit current and other point of connection data
1.18 | Persons participating in Preliminary meeting (This is filled in during Preliminary meeting)
| 1.18.1 | RSO/DSO
| 1.18.2 | Connectee
| 1.18.3 | Date and time of the meeting
*) In VJV/SJV2024 DSO/RSO may set many requirements it is not required that DSO/RNO has set all sections
2 | Top-level Control Philosophy |  |  | VJV2024 | SJV2024 | Distribution system Operator / Relevant System Operator requirement or reference* | Project (BOP design) | OEM 1 | OEM 2 | OEM 3
2,1 | Reference point(s) for Active power Control (POM(s))
2,2 | Reactive power limits at the point of connection (reactive power window)? How this is taken into account in control design?
2,3 | How many Power Park Controllers (PPC) will there be at site?
2,4 | Is the PPC supplier same as the converter supplier?
2,5 | Is there redundancy or fall-backs regarding to Power Park Controllers (PPC) if e.g. Master controller fails?
2,6 | What happens for the Power Park Controller (PPC) in event of measurement failure? |  |  | Chapter 18 | Chapter 13
3 | Balance of Plant |  |  | VJV2024 | SJV2024 | Distribution system Operator / Relevant System Operator requirement or reference* | Project (BOP design) | OEM 1 | OEM 2 | OEM 3
3,1 | Main transformers
| 3.1.1 | What is the Un at HV-side? |  | Chapter 10
| 3.1.2 | Start point arrangements; Reactor needed ?
| 3.1.3 | Is there On-load tap changer (OLTC)?
| 3.1.4 | Connection to overhead line or middle of cable?
If yes, is the transformer zk high enough for DSO/RSO protection selectivity requirement?
3.2 | Protection design shall consider that the plant will not trip during LVRT/HVRT, voltage and frequency dips or other grid events
| 3.2.1 | Note new high voltage ride through requirement
| 3.2.2 | Has "Local disconnection relay" included?
3.3 | Voltage and active power control implemented at site CT's and VT's ?
4 | General Performance requirements |  |  | VJV2024 | SJV2024 | Distribution system Operator / Relevant System Operator requirement or reference* | Project (BOP design) | OEM 1 | OEM 2 | OEM 3
4.1 | Reactive power requirement – Does the DSO/RSO specify a reactive power capacity requirement? Is the project aware of how this requirement affects asset design, especially if the connection agreement is in MVA? |  |  | Chapter 17
| 4.1.1 | Reactive Control mode and tuning principles set by DSO/RSO |  | Chapter 17
4.2 | Is the supplier aware of the active power prioritization requirement, if the LVRT mode is not activated? |  |  | Chapter 10 and 18
4.3 | Is this the first time the inverter supplier and power park controller supplier deliver a project together?
| 4.3.1 | If yes, are you aware of communication risks regarding to delays and grid compliance and market participation? How to mitigate the risk?
| 4.3.2 | If no, how to ensure that voltage control and active power response requirement is met regarding to communication/protocol delays?
5 | Performance requirements |  |  | VJV2024 | SJV2024 | Distribution system Operator / Relevant System Operator requirement or reference* | Project (BOP design) | OEM 1 | OEM 2 | OEM 3
5.1 | Is the supplier aware of any DSO/RSO requirement for voltage control any other reactive power control mode? |  |  | Chapter 18 | Chapter 12 and 13
|  | Has the supplier confirmed e.g. by simulation models and FAT tests that they have the technology for the requirement? |  | Chapter 18 | Chapter 13
5.2 | Is the supplier aware of the new fault current infeed requirements? |  |  | Chapter 10 | Chapter 10
5.3 | Has the new HVRT requirement noted in the design? Is the turbine/converter OEM aware of this? |  |  | Chapter 10 | Chapter 10
5.4 | Is this the first time the inverter supplier and power park controller supplier deliver a project together?
| 5.4.1 | If yes, are you aware of communication risks regarding to delays and grid compliance? How to mitigate the risk?
6.6 | How to ensure safe disconnection from the grid if there will be Islanding?
7 | Remote Controllability and Power Park controller |  |  | VJV2024 | SJV2024 | Distribution system Operator / Relevant System Operator requirement or reference* | Project (BOP design) | OEM 1 | OEM 2 | OEM 3
7.1 | Is the power park controller supplier aware of DSO/RNO signals required to be exchanged / controlled by the operator? |  |  | Chapter 10 | Chapter 10
7.2 | Is the Relevant Operator (RO) aware of DSO signals required to be changed/ controlled? |  |  | Chapter 10 | Chapter 10
| 7.2.1 | Disconnection from Grid or Stop From RO to site with Phone contact / From DSO/RNO to RNO over signals / not implemented |  | Chapter 10 | Chapter 10
| 7.2.2 | Active power limitation From RO to site with Phone contact / From DSO/RNO to RNO over signals / not implemented |  | Chapter 10 | Chapter 10
| 7.2.3 | Reactive power control mode From RO to site with Phone contact / From DSO/RNO to RNO over signals / not implemented |  | Chapter 10 | Chapter 10
| 7.2.4 | Other? |  | Chapter 10 | Chapter 10
7.3 | Is control prioritization between RO,OEM, Aggregator etc. clear how to implement it in the PPC ? |  |  | Chapter 10 | Chapter 10
7.4 | Autonomous connection after losing external network connections has this been designed? |  |  | Chapter 10 | Chapter 10
7.5 | Who is responsible to deliver real-time data to Fingrid. DSO/RNO or Connectee? Is Fingrid signal manual familiar to project? https://www.fingrid.fi/kantaverkko/liitynta-kantaverkkoon/tekniset-vaatimukset/jarjestelmateknisia-vaatimuksia-taydentavat-dokumentit/ |  |  | Chapter 10 | Chapter 10
8 | Telecommunications and information security |  |  | VJV2024 | SJV2024 | Distribution system Operator / Relevant System Operator requirement or reference* | Project (BOP design) | OEM 1 | OEM 2 | OEM 3
8.1 | Telecommunications and information security - has this been considered? |  |  | Chapter 10 | Chapter 10
| 8.1.1 | See Cybersecurity survey from https://www.fingrid.fi/kantaverkko/liitynta-kantaverkkoon/tekniset-vaatimukset/jarjestelmateknisia-vaatimuksia-taydentavat-dokumentit/ |  | Chapter 10 | Chapter 10
8.2 | Have you considered any redundancy for the connections?
8.3 | Has project familiar with Requirements for the Reliability of Reserve Provision? |  |  | Not SJV/VJV related)
| 8.3.1 | See material from Fingrid reserve market details https://www.fingrid.fi/sahkomarkkinat/reservit/reservituotteet-ja-markkinoille-osallistuminen/ |  | Not SJV/VJV related)